## 000-E-GRD-70006-001-RAP-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 3 | Adnan Alothman | As per the Contract, Annex1-Technical documents do not have any order of precedence. Please correct this to align with EPC Contract.
2 | Callout | 8 | Adnan Alothman | For all critical equipment, company representative attendance is required as per BMPS-B11.
3 | Text Box | 1 | Ahmed Marhoon | The following are comments related to instrumentation and control. Contractor is requested to update the other documents issued as part of this transmittal, in addition to Datasheets, based on the comments stated herein and ensure consistency prior to release of MR to suppliers. 1. Add a clear note on Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. Requirement of MCM to be verified with the supplier. Reference to BMPS-J15 MCM to be added. 2. Instruct the supplier to source instrumentations from project AVL only. 3. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this MR shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 4. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 5. All the BN machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 6. Narrative/flow charts/cause and effect, in client formats, shall be provided for any control or sequence logic. 7. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting …etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 8. In addition to BMPS-J6 and J2, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J3, J8, J9, J15 ... etc. All instruments and control systems to be designed according to BMPS specifications. 9. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 10. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval.
4 | Call-out | 5 | Ahmed Marhoon | HV Electric shall not be part of Instrumentation and accessories.
5 | Call-out | 8 | Ahmed Marhoon | What about ESD, if any?
6 | Call-out | 8 | Ahmed Marhoon | What about HAZOP/SIL/CHAZOP?
7 | Call-out | 8 | Ahmed Marhoon | IFAT
8 | Call-out | 8 | Ahmed Marhoon | What about equipment requiring fireproofing per the FEE classification and being supplied by vendor?
9 | Cloud+ | 8 | Ahmed Marhoon | These activities are major milestones for the package and it is mandatory to be attended by Client representatives. Attendees list to be updated based on the agreed project responsibility matrix.
10 | Call-out | 21 | Ahmed Marhoon | Contractor is requested to validate the models quoted for the instrumentation and ensure that the latest models are supplied for BMP in accordance to the projects specifications. To avoid supplying an obsolete and/or products at their obsolescence phase, vendors to be instructed to provide Products Life-Cycles/Road-maps. For example, model YTA310 for ESD Transmitter has recently announced obsolete and needs to be replaced with the latest model number. This is a general comment that need to be globally addressed by the contractor.
11 | Text Box | 18 | Hasan Asad | Basis the fan criticality to operation and fan non-availability consequence, quote for electric motor and reducer gear shall be provided as optional.
12 | Text Box | 20 | Mahdi Ali | Change orientation of this page
13 | Callout | 2 | Mohamed Ayyash | INDEX PAGE 2/23 ITEM 2: Typo, should read "OBJECTIVE" and not OBJECT.
14 | Callout | 2 | Mohamed Ayyash | INDEX page 2/23 item 10.1 should read "Commissioning and Start-up" and not vise versa.
15 | Callout | 3 | Mohamed Ayyash | PAGE 3/23 ITEM 2: Typo, should read "OBJECTIVE" and not OBJECT.
16 | Callout | 18 | Mohamed Ayyash | Item 10.1 page 18/23 should read "Commissioning and Start-up" and not vise versa.
17 | Callout | 18 | Mohamed Ayyash | Item 10.1 text page 18/23 Add the word "Commissioning to the sentence
18 | Text Box | 12 | Sankara | Specify the hazardous area classification and comply with BMPS-P2.
19 | Callout | 4 | Yousif Ahmadi | Per BMPS-E8 ADDENDUM TO CES EXH-SU-1317-K this should be replaced with "Headers and laterals shall be PVC or PP"
20 | Callout | 9 | Yousif Ahmadi | Add: Provided that the Vendor has been qualified for use on the SATORP project or a Saudi Aramco or Chevron project for a similar service and in a comparable facility to BMP