## 000-E-GRD-80007-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | always add document title in the header
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
3 | Text Box | Page 3 | Dowon Pyun | Company General Comments; 1. Contractor to finalize the width of piperack at the earliest. This will not only help the downstream work progress of the Contractor, but will also eliminate the time loss in the bid evaluation through the fairness of quotation from air cooler Suppliers. 2. The Contractor is required to receive the thermal calculation results throughout Vendors quotation to complete early verification works for the thermal ratings. 3. Considering inland transportation, erection, future maintenance and Vendor's equality opportunity for their bidding, bay/bundle size and weight shall be restricted. Contractor to confirm this. 4. Direct loads transferring from piping manifold to bundle header boxes shall be minimized within the ranges permitted in API 661 and Contractor shall confirm the maximum load conditions to cover external loads under the conditions of Vendor's himself design.
4 | Callout | Page 5 | Dowon Pyun | Contractor to show document no.
5 | Text Box | Page 5 | Dowon Pyun | There are many document numbers specified as PTC-XXX in the scope of supply or particular technical specification, but they are actually not shown in the document list of requisition. This is typical comment to other requisitions.
6 | Callout | Page 6 | Salman Jaffer | Please refer to Bid Query T1383 for the requirement for automatic louver
7 | Cloud+ | Page 6 | Julio.Aguilar | Supplier
8 | Cloud+ | Page 6 | Sameer.Ahmed | Remove V belts
9 | Callout | Page 6 | Dowon Pyun | Usually flooring grating is handled by Civil. Contractor needs to confirm internally the scope of responsibility and Company recommends the installation of flooring grating in the entire area where air coolers are installed. Compared to cross type walkway, it is excellent in Contractor's constructability and will be helpful for future maintenance by Company
10 | Call-out | Page 6 | Ali Abbas | Louvers shall be fitted with FF type smart positioner with full diagnostic as per BMPS J specification/standard drawings/AVL to meet project design with position indication in the DCS. I/P not to be used. Need to attached applicable BMPSs and also reference Inst Air pressure for the actuator design.
11 | Callout | Page 7 | Salman Jaffer | Please add (Free draining whenever applicable per the data sheet or PIDs
12 | Call-out | Page 7 | Ali Abbas | Refer to spec for SS type
13 | Callout | Page 7 | Syed Ahmed | Local start/stop switch box at platform, stop switch box at grade level and stop DCS switch.
14 | Callout | Page 7 | Syed Ahmed | The nameplate shall be made of stainless steel and be fixed to a non-removal part of the frame.in addition, motor with VFD shall be provided with additional nameplate information showing related data. as per BMPS -P19
15 | Callout | Page 7 | Dowon Pyun | When transition beams are installed, the maintenance floor shall NOT be stepped.
16 | Text Box | Page 7 | Hasan Asad | Add: Spare interchangeable belts
17 | Callout | Page 9 | Dowon Pyun | requisition
18 | Callout | Page 9 | Dowon Pyun | Contractor to add project specification 2520-Z000-MS6740-52, Material Preservation during Construction, Pre-commissioning and Commissioining. Accordingly this statement shall be corrected and Company considers that the start period is based on the completion of on-site delivery.
19 | Callout | Page 10 | BD Mori | Based on the highest temperature expected at inlet to the cooler at transient operating conditions or upset scenario e.g start-up, shutdown, electrical power failure or any other operating scenario specified in the air coolers data sheets, if required the vendor shall perform FEA analysis.
20 | Callout | Page 10 | Dowon Pyun | Delete this paragraph since noise requirement is covered by next para. 5.6
21 | Text Box | Page 11 | Antony.Bentley | Earthquake loads need not be considered BMPS-M1 - 7.15
22 | Arrow | Page 11 | Antony.Bentley
23 | Cloud+ | Page 11 | Julio.Aguilar | Replace by "Supplier" throughout all document
24 | Callout | Page 11 | Sameer.Ahmed | Addition (as applicable) loads described in BMPS-A1 Section 10.7 to be considered
25 | Text Box | Page 11 | Hasan Asad | Add: Fan and Motor bearings lubrication points shall be extended to the platform level for on-line greasing.
26 | Callout | Page 11 | Dowon Pyun | Insert "In addition to documents and drawings supply required in 000-E-SOW-80007-001-RAP,"
27 | Text Box | Page 12 | Hasan Asad | Portable heavy lifter shall be provided for ease of rigging of motor, fan, etc.
28 | Text Box | Page 14 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
29 | Cloud | Page 15 | Mahdi Ali
30 | Callout | Page 15 | Sameer.Ahmed | Why cooler 371E0001 is not included in this list? TTSJV to advise if this cooler will be purchased under another MR
31 | Text Box | Page 16 | Hasan Asad | SAT for entire bank rotating units and structure to verify structure and equipment vibration levels.
32 | Text Box | Page 18 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
33 | Text Box | Page 20 | Hasan Asad | Applicable to all data sheets comments: 1. Lubrication points shall be extended to platform level for ease of lubrication without shutting down the equipment. 2. Vibration pick-up points shall be accessible for routine condition monitoring. 3. SAT shall be performed including machinery vibration, bearing temperature, alignment verification, belt tightness test, etc.