## 000-F-GRD-60002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 8 | Omran A | System
2 | Text Box | 9 | Omran A | 1-Status of aviation light (ON/OFF or Healthy/Faulty) shall be integrated to the Control system such as DCS or SCADA, etc.... 2-For the safe operation of business units, Dual Aviation lights with dual/independent power feeder/supply shall be installed
3 | Call-out | 14 | Ali Hasan | Pilot ignition, detection and integration with the heater BMS to be included in the Scope of Supply, and narrative for the control/firing sequence to be provided.
4 | Call-out | 14 | Ali Hasan | Pilot detector sensor, using ionization rod or flame eye, shall be included in the Scope of Supply. Both detection type shall be evaluated during the design review.
5 | Text Box | 14 | Ahmed Habib | CHAZOP/SIL
6 | Text Box | 15 | Ahmed Habib | Dual Power supply feeder required from independent power feeders
7 | Text Box | 15 | Ahmed Habib | For Manual ESD Trip, Pull button (2oo3 contact) shall be provided
8 | Text Box | 15 | Ahmed Habib | ESD UPS
9 | Text Box | 15 | Omran A | As per BMPS-J22
10 | Text Box | 16 | Omran A | Backup & Restore procedures for all control systems. Also, RAMS (Risk Assessment and Method Statements)
11 | Call-out | 16 | Rashed Almudahka | refer to UOP specification 2-12-6 and include spares as per clause 6.1. point t(5) and clause 6.4. point a(5).
12 | Text Box | 17 | Omran A | & CHAZOP
13 | Text Box | 18 | Omran A | CHAZOP &
14 | Text Box | 18 | Omran A | CHAZOP &
15 | Text Box | 33 | Ahmed Habib | Control Systems to be added