## 000-F-GRD-70001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Yousif Ahmadi | Numbers to be changed to new equipment numbering
2 | Text Box | 1 | MAK | Use the latest cover page template that is part of the Homogenization Procedure. MOC shall coordinate with JV Directorate.
3 | Text Box | 1 | Raj | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3.
4 | Text Box | 3 | Ahmed Marhoon | The following are comments related to instrumentation and control. Contractor is requested to update the other documents issued as part of this transmittal, including the data sheets, based on the comments stated herein and ensure consistency prior to release of MR to suppliers. 1. All applicable BMPS from J class to be added for the supplier to comply with. e.g. J1, J2, J3, J9 ... etc. All instruments and control systems to be designed according to BMPS specifications. 2. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Client standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 3. Note to be added that all heaters to have access ladder and platform for all 4 inch nozzles in the stack used for PEMPS or CEMS. The nozzle location for PEMS/CEMS to be coordinated/finalized with the PEMS/CEMS vendor. 4. The way the exclusion list is stated in this document results in misunderstandings and leads to unclear SOW. e.g. BMS Hardware Vs. Instrumentation Line of SOW document of this Transmittal. 5. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS for the ID fans in addition to vendor requirement. 6. Supplier to be instructed to source all instrumentation from the approved AVL for BMP. 7. List of documents, hardware, software and services to comply with the BMPS specifications (including tests and certifications). 8. Reference to BMPS-J10 Wireless to be added. Supplier to be notified on the criteria being development for instruments that can be accepted as wireless for non-critical measurement. 9. Supplier to be consulted for the technical specifications of the Analyzers. Also the tapping point is specified for Oxygen/CO, it should be corrected to Oxygen/Combustible. 10. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this MR shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 11. Narrative/flow charts/cause and effect shall be provided, in Client standard formats, for any control or sequence logic. 12. For damper actuator, I/P is specified. The actuator shall be fitted with a smart positioner as per spec and not I/P transducer. 13. The design of the minimum stops (mechanical/soft-clamp) for passes to be finalized at a later stage. 14. Compliance to licensors mandatory and recommended requirements to be included. 15. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting &etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 16. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 17. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval.
5 | Call-out | 3 | Ali Abbas | One set of O2/Comb. per cell/bank.
6 | Cloud+ | 4 | A.Jabbar Mahmood | Residue HCU is not applicable for this particular MR
7 | Call-out | 4 | Mahdi Ali | Do not use FEED number.
8 | Cloud+ | 4 | Yousif Ahmadi | The correct number is 019E0016. Check and confirm
9 | Cloud+ | 4 | Yousif Ahmadi | The correct number is 019E0015. Check and confirm
10 | Callout | 5 | Adnan Alothman | As per the Contract, Annex1-Technical documents do not have any order of precedence. Please correct this to align with EPC Contract.
11 | Call-out | 6 | Sameer Foujdar | APH washing procedure and safety precautions to be taken during washing to be included in the Operation Manual.
12 | Cloud+ | 6 | Ahmed Marhoon | C&E diagram to be in owner format.
13 | Call-out | 9 | Ahmed Marhoon | Add CHAZOP
14 | Call-out | 9 | Mahdi Ali | Remove 'D' from Unit number
15 | Cloud+ | 14 | A.Jabbar Mahmood | P&IDs not attached for owner review. Shall be attached in the next revision.
16 | Call-out | 14 | A.Jabbar Mahmood | As per the P&IDs, guillotines are also provided on the suction ducts for each FD Fan. Check and update.
17 | Call-out | 14 | A.Jabbar Mahmood | As per the P&IDs, no guillotines are indicated on the inlet/outlet to/from stack. Check and confirm.
18 | Cloud+ | 15 | A.Jabbar Mahmood | Correct the wording to "combustion air"
19 | Call-out | 15 | A.Jabbar Mahmood | As per the P&IDs, hot end also has thermocouples at the flue gas inlet.
20 | Call-out | 16 | Ebrahim | the AC outgoing power supply from UPS is 115V, 50Hz
21 | Call-out | 16 | Mahdi Ali | Incorrect Bapco document number
22 | Call-out | 18 | Ahmed Marhoon | Add CHAZOP
23 | Call-out | 18 | Ahmed Marhoon | What about BMS/ESD?
24 | Call-out | 18 | Ahmed Marhoon | What about IFAT?
25 | Callout | 18 | Adnan Alothman | For all critical equipment, company representative attendance is required as per BMPS-B11.
26 | Call-out | 19 | Ahmed Marhoon | A comprehensive list of exclusions to be added to the MR. e.g. What does BMS Hardware refer to? ESD system or even the field instruments?
27 | Call-out | 23 | Mahdi Ali | Remove 'D' from Unit number
28 | Call-out | 23 | Mahdi Ali | Remove 'D' from Unit number
29 | Cloud+ | 24 | Ahmed Marhoon | Referenced point (3.9.9) could not be found on this document.
30 | Cloud+ | 25 | A.Jabbar Mahmood | Residue HCU is not relevant for this MR
31 | Call-out | 25 | Mahdi Ali | Typo
32 | Callout | 26 | Yousif Ahmadi | RHCU is irrelevant
33 | Callout | 28 | Yousif Ahmadi | Change chapter number to 3.8.7
34 | Text Box | 29 | Hasan Asad | 2 probes shall be installed for thrust bearings. BMPS A3 and vendor recommendation shall be considered.
35 | Text Box | 29 | Hasan Asad | The Supplier/Vendor shall include the lubrication system, cooling system, etc in the quotation.
36 | Call-out | 31 | Ahmed Marhoon | Operator Training "Simulator". Also add reference to BMPS-J32.
37 | Text Box | 31 | Hasan Asad | LCCA report for 20 years shall be provided to serve as element for proposal selection and for maintenance strategy consideration.
38 | Text Box | 32 | Sankara | Ex-p motors are not acceptable as per agreed change in BMPS-P18. Refer bid clarifications.
39 | Call-out | 32 | Ahmed Marhoon | Emphasize on the system architecture to be in accordance with the BMPS-J33 with regard to integration with/in ESD.
40 | Call-out | 32 | Mahdi Ali | Remove 'M' from the Unit number
41 | Callout | 32 | Yousif Ahmadi | Delete the repetition
42 | Callout | 35 | Yousif Ahmadi | RHCU is irrelevant
43 | Text Box | 37 | Hasan Asad | Basis FD & ID Fans criticality and fan non-availability consequence on heater/unit operation, a complete rotor element shall be quoted as optional price.
44 | Call-out | 42 | Sameer Foujdar | APH washing procedure and safety precautions to be taken during washing to be included in the Operation Manual.