## 000-H-GRD-70001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | Unit numbers shall always be 3 digits
2 | Text Box | 1 | Mahdi Ali | always include the document title in the header | Part of template - To be checked by Directorate [JVD Reply] Template will be issued by JV DCC, After receiving the revised template, it will be updated. | N
3 | Text Box | 1 | Ahmed Marhoon | The following are comments related to instrumentation and control. Contractor is requested to update the other documents issued as part of this transmittal based on the comments stated herein and ensure consistency prior to release of MR to suppliers. 1. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this MR shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 2. Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 3. Supplier to be instructed to generate, if applicable, all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 4. Contractor is requested to validate the models quoted for the instrumentation and ensure that the latest models are supplied for BMP in accordance to the projects specifications. To avoid supplying an obsolete and/or products at their obsolescence phase, vendors to be instructed to provide Products Life-Cycles/Road-maps. For example, model YTA310 for ESD Transmitter has recently announced obsolete and needs to be replaced with the latest model number. This is a general comment that need to be globally addressed by the contractor. 5. Supplier to comply with all the applicable BMPSs and provide, as a minimum, all the documents, hardware, software and services according to the relevant sections of the BMPSs in the agreed standard formats of the project. List to reflect all the required deliverables in accordance to BMPS. 6. Inspection and Test Plan to include the participation of the client in accordance with the BMP agreed procedures. Loop testing plan to be detailed. | Contractor ensures consistency between different documents of requisition. 1. Final P&ID will be submitted by Vendor, including all its scope and approved by CONTRACTOR. CONTRACTOR will check that HAZOP actions shall be correctly implemented. All BMPS applicable are part of the Material Requisition and included in section named MRQ. 2. Noted. Already included in VDDR. 3. All instrument Data Sheet and any other information required for instruemtns is already included as required in the VDDR (MRQ). 4. Models in AVL will be checked and updated by JVD. [JVD Reply]YTA-310 should be replaced with YTA-610. 5. Requested in GRD document next revision. 6. Noted. | Y
4 | Text Box | 1 | Raj | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3. | Noted. | Y
5 | Callout | 2 | Mohamed Ayyash | Delete dots | Noted and corrected in next revision. | Y
6 | Text Box | 3 | Mahdi Ali | General Note: Unit number shall have 3 digits | Noted and corrected in next revision. | Y
7 | Callout | 3 | Adnan Alothman | As per the Contract, Annex1-Technical documents do not have any order of precedence. Please correct this to align with EPC Contract. | Part of template - by Directorate | N
8 | Cloud+ | 4 | bapco-user | To be checked/ changed per new numbering sequence | Tags numbers cannot be changed | N
9 | Callout | 4 | Mohamed Ayyash | ??? | Noted and corrected in next revision. | Y
10 | Cloud+ | 4 | bapco-user | 011E0003 A-F per ITB and to be checked with new numbering | Noted and corrected in next revision. | Y
11 | Call-out | 4 | 986131 | Add a note: For 011U0001: The Package includes as minimum the above items: The final number of stages required and the equipments to be confirmed by the vendor. | Noted and implemented in next revision. | Y
12 | Callout | 5 | Mohamed Ayyash | Add "commissioning" | Noted and implemented in next revision. | Y
13 | Call-out | 5 | 986131 | Process design review and recommended configuration for the 011U0001 | Noted and implemented in next revision. | Y
14 | Call-out | 5 | Ahmed Marhoon | Add the applicable BMPS-Js specifications and instruct the supplier to strictly comply with the specs. Also add notes clarifying the DCS/ESD scheme of BMP, SPI requirements and the need to generate documents in clients' standard formats. | Applicable BMPS-J specifications are already included in MRQ document of requisition. | Y
15 | Callout | 5 | Adnan Alothman | For all critical equipment, company representative attendance is required as per BMPS-B11. | It will be cheked and modified by JV in order to be implemented in the template. Vendor will be advise during TBE stage. | Y
16 | Call-out | 6 | Ali Abbas | Add Owner resp. | It will be cheked and modified by JV in order to be implemented in the template. Vendor will be advise during TBE stage. | Y
17 | Call-out | 6 | Ahmed Marhoon | Add CHAZOP | CHAZOP is not applicable to this RFI. ( PLC or MMS is not VENDOR scope) | N
18 | Call-out | 6 | Ahmed Marhoon | What about I-FAT? | I-FAT is not applicable to this RFI. ( there are no control systems in VENDOR scope) | N
19 | Call-out | 6 | Ahmed Marhoon | Comprehensive list to be developed. | To be developed for RFP after agreement of the scope with vendor. | Y
20 | Call-out | 7 | A.Jabbar Mahmood | Not provided in this document and hence not reviewed by the owner | Referred document is part of the order, to be added by procurement Dept. | Y
21 | Call-out | 8 | Ahmed Marhoon | All applicable BMPS-Js to be added. | Applicable BMPS-J specifications are already included in MRQ document of requisition. | Y
22 | Callout | 10 | Mohamed Ayyash | ?? | Corrected in next revision. | Y
23 | Call-out | 12 | 986131 | ADD: Ejector performance Test and Report. | To be implemented by Directorate. Vendor will be informed during TBE stage. [JVD Reply] refer to reply in 000-H-ITP-70001-001-RAP-CS. 000-H-ITP-70001-001-RAP-CS, this file will be sent separately. It is under discussion between each OC's Inspection engineer. | N
24 | Callout | 13 | Mohamed Ayyash | No. (Typo) on all pages | Corrected in next revision. | Y
25 | Call-out | 13 | 986131 | ADD: Ejector performance curves. | Requested in SOW document. | Y
26 | Callout | 14 | Mohamed Ayyash | Should read Commissioning and Start-up (not vise versa) | Corrected in next revision. | Y
27 | Callout | 14 | Mohamed Ayyash | Add "Commissioning" | Corrected in next revision. | Y
28 | Text Box | 15 | Hasan Asad | LCCA shall be provided by Supplier. Spare parts shall include one run as this package will undergo inspection with the unit turnaround. | It´s in CONTRACTOR deliverable. Vendor only supply the information to preapre the LCCA | N