## 000-K-ITP-70001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Mohamed Ayyash | No. (Typo) apply to all sheets | Not aplicable. This is not a typo mistake | N
2 | Callout | 1 | Mohamed Ayyash | What is 000M? should be 7CDU/2HCU | This is not applicable. This is a generic designation of the document assigned by TTSJV DCC and cannot be modified. | N
3 | Text Box | 1 | Ahmed Marhoon | Inspection and Test Plan to include the participation of the client in accordance with the BMP agreed procedures. Loop testing plan to be detailed. Tests related to instrumentation, control and safety to comply with the BMPS J series specifications/instructions. As a minimum, the relevant Checklist as agreed for the BMP shall be referenced in the ITP. For example, BMPS-K-50409 is applicable for the Reciprocating Compressors. This is a typical comment for all ITPs. | A dedicated column for CLIENT's involvement in each activity/test shall be assigned by TTSJV DCC (template cannot be modified). Tests shown in this ITP document are as per BMPS-K-50409 and applicable project specifications. Check lists are not part of ITP. Detailed tests and activities shall be developed by VENDOR and submitted in QCP document during Engineering phase | N
4 | Callout | 2 | Mohamed Ayyash | Complete line | Noted, it shall be revised in following document revision | Y
5 | Text Box | 2 | Hasan Asad | The Compressor Complete unit commissioning shall be supervised by Vendor/Supplier. | The required tests for compressor during pre-commisioning, commisioning and start-up phases are part of CONTRACTOR's scope of supply, and therefore it cannot be added to this ITP (the ITP shows tests under manufacturer's responsability in accordance with BMPS and international standards). Manufacturer supervision shall be considered during those phases. | N
6 | Callout | 2 | Mohamed Ayyash | Correct | Noted, it shall be revised in following document revision | Y
7 | Callout | 2 | Yousif Ahmadi | Add Pre-shipping inspection | It will be cheked and modified by JV in order to be implemented in the template. Vendor will be advise during TBE stage | N
8 | Cloud+ | 3 | Yousif Ahmadi | Add "R" against following WPS/PQR ...... Inspection procedures ... Welding consumable ... | It will be cheked and modified by JV in order to be implemented in the template. Vendor will be advise during TBE stage | N
9 | Callout | 19 | Mohamed Ayyash | Overlap with line (Correct) | Noted, it shall be revised in following document revision | Y