## 000-S-GRD-70009-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Raj | Owner has reviewed and commented on the MR package submitted on Contractor’s request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3.
2 | Callout | 1 | Sankara | PACKAGE
3 | Callout | 1 | Mohamed Ayyash | No. (Typo) apply to all sheets
4 | Callout | 1 | Mohamed Ayyash | Should read 7CDU
5 | Callout | 2 | Mohamed Ayyash | Should read "Commissioning and Start-up" and not vise versa
6 | Callout | 3 | Adnan Alothman | As per the Contract, Annex1-Technical documents do not have any order of precedence. Please correct this to align with EPC Contract.
7 | Call-out | 4 | Ali Abbas | design per BMPSs J class and associated standard and typical drawings.
8 | Call-out | 4 | Ali Abbas | Add owner
9 | Callout | 4 | Adnan Alothman | For all critical equipment, company representative attendance is required as per BMPS-B11.
10 | Call-out | 4 | Tapas | Vendor to design and chose the right combination between bielectric and EDD to meet the final specification specified in the data sheet. The basis of design document to be submitted which clearly states the rational for the configuration selected.
11 | Call-out | 4 | Ali Abbas | all applicable documents listed in the CDRL to be provided.
12 | Call-out | 4 | Ali Abbas | Detailed narratives, sequence logics, flow charts for control, sequence and trip logics. This narrative to be used for DCS and other safety system configurations.
13 | Call-out | 4 | Tapas | ADD: Rag layer detection and removal system engineering design and supply.
14 | Callout | 5 | Mohamed Ayyash | add space
15 | Call-out | 5 | Tapas | and/Or Electro Dynamic Desalter (EDD)
16 | Call-out | 5 | Ahmed Marhoon | What about DCS IFAT?
17 | Callout | 5 | alexis.martinez | The Equipment Numbers need to be updated as per the new numbering provided by owner
18 | Call-out | 5 | Ahmed Marhoon | Add CHAZOP
19 | Callout | 6 | alexis.martinez | Include the unit number (010) to each mixing valve TAG number
20 | Call-out | 6 | Sameer Foujdar | Mixing valve number is PDV0035 to be corrected and rectified.
21 | Callout | 6 | alexis.martinez | If the vendor consider the requirement of additional mixing device after mixing valve e.g. static mixer, this device have to be included in the list to supply by vendor.
22 | Call-out | 6 | Tapas | ADD: Rag layer detection and removal system along with the necessary piping, fittings, valves, instrumentation and accessories.
23 | Call-out | 7 | Ali Abbas | for loops classified as eligible for wireless to be identified.
24 | Call-out | 7 | Tapas | Add: and reliable
25 | Call-out | 7 | Ali Abbas | Instrumentation installation and access per BMPSs and typical/standard drawings.
26 | Call-out | 12 | Ali Abbas | For rotating equipment reference the requirement for MCM stated in BMPS-A3
27 | Call-out | 16 | Ali Abbas | including deviation from our BMPSs and typical/standard drawings
28 | Callout | 16 | Mohamed Ayyash | Should read "Commissioning and Start-up" and not vise versa
29 | Callout | 17 | Mohamed Ayyash | Add "Commissioning" to the sentance
30 | Callout | 17 | Mohamed Ayyash | Should the commissioning phase be also covered ?
31 | Text Box | 18 | Hasan Asad | The vendors shall provide complete LCCA report to serve for selection and procurement requirement and as input for design and maintenance requirement.
32 | Text Box | 18 | Ahmed Marhoon | The following are comments related to instrumentation and control. Contractor is requested to update the other documents issued as part of this transmittal, in addition to the data sheet, based on the comments stated herein and ensure consistency prior to release of MR to suppliers. 1. All applicable BMPS-J series to be referenced (such as J8, J3, J31 …etc) for the supplier to comply with. 2. Instruct the supplier to source instrumentations from project AVL only. 3. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this MR shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 4. Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 5. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting …etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 6. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 7. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval. 8. Scope of Work to be consistent with the PID representation. PID/SOW/GRD to be updated to reflect the same scope.