## 000-S-ITP-70009-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Casella di testo | 1 | LPetroni | AP
2 | Text Box | 1 | Sankara | Inspection Level shown as 4 in subsequent pages to be corrected as 3
3 | Casella di testo | 1 | LPetroni | AP
4 | Callout | 1 | Mohamed Ayyash | No. (Typo) apply to all sheets
5 | Callout | 1 | Mohamed Ayyash | Should read 7CDU
6 | Text Box | 1 | Hasan Asad | Inspection and Test requirement shall be advised basis vendor detailed design.
7 | Callout | 2 | Yousif Ahmadi | Add to before fabrication: WPS/ PQR/ weld map "R"
8 | Text Box | 2 | Ahmed Marhoon | Inspection and Test Plan to include the participation of the client in accordance with the BMP agreed procedures. Loop testing plan to be detailed. Tests related to instrumentation, control and safety to comply with the BMPS J series specifications/instructions. As a minimum, the relevant Checklists as agreed for the BMP shall be referenced in the ITP. For example, BMPS-J-50365 is applicable for the Control Valves. Any deviation/deficiency from the BMPS shall be highlighted to Client for review/approval.
9 | Callout | 2 | Yousif Ahmadi | Add Pre-shipping inspection
10 | Cloud+ | 8 | Ahmed Marhoon | Details are not matching the relevant Checklist provided as part of the BMPS Spec. To be clarified by TTSJV Refer to comment on the Inspection and Test Plan provided on sheet 2/12 of this document. This is a typical comment applicable to all ITPs.