## 010-E-DAT-00031-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 3 | 986131 | ADD: (loss of crude feed)
2 | Call-out | 2 | 986131 | API 661 restricts the face velocity to 700 ft/min for forced draft. Report the actual ft/min velocity and confirm that it meets the API requirement.
3 | Call-out | 2 | 986131 | As normal duty and turn down duty is much lower provide adequate air flow control
4 | Call-out | 3 | Mahdi Ali | Do not use FEED drawing number
5 | Text Box | 1 | 986131 | Fill in the Air-Cooler Heat exchanger checklist as given in API 661 and submit along with the data sheet.
6 | Call-out | 2 | 986131 | Fin fan width reduced by 70% from feed. please explain the rational
7 | Callout | 1 | Mohamed Ayyash | General Comment: Fonts are too small throughout the data sheets and unreadable.
8 | Text Box | 3 | Ahmed Marhoon | Note 7: The scope for instrumentation and control is not limited to the alarms in DCS. All the control functions will be done in the DCS with the necessary interconnections with the electrical MCC. The final design of the system shall be based on the BMPS specifications (including relevant J class) and the final PID post detail design and Hazop3/SIL analysis. Suppliers to be instructed accordingly. This is a typical comment for all fin fan air coolers. Note12: Contractor to add reference to the applicable BMPS specifications such as BMPS-P20/P21 and relevant BMPS-J specifications. Typical for all air coolers with Variable Speed Drives.
9 | Cloud+ | 2 | 986131 | Note of the data is filled in this section. For this application (diesel cooling) is Contractor considering recirculation system/ steam coil? Please confirm.
10 | Cloud+ | 3 | Mohamed Ayyash | Page 3/3 notes 8, 9 and 10 to be align for better representation inline with other notes.
11 | Cloud+ | 2 | Yousif Ahmadi | Per DEED data sheet number of inlet and outlet nozzles are 2 each. check and confirm
12 | Call-out | 2 | 986131 | Please refer to the API 661 data sheet (page 2 of 2) and add all the required fields under Controls air side
13 | Callout | 1 | Mohamed Ayyash | Top of cover page: add Unit name 7CDU. Apply to all sheets.