## 018-E-DAT-00001-001-RAP-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 2 | Fatema Hashem | CORRECT THE FLUID NAME TO MP/MT VAPOUR
2 | Callout | 2 | Fatema Hashem | CLG SPECIFIED METALLIC FAN BLADES. ALTHOUGH BAPCO REQUESTED FOR FRP, ADVISE IF LICENSOR CONCURRENCE HAS BEEN OBTAINED TO CHANGE THE BLADE MATERIAL
3 | Call-out | 2 | Rashed Almudahka | two fans per bay as per OWNER reply to T1265 and as per Licensor EDP.
4 | Text Box | 3 | Sankara | VFDs shall be installed indoors inside the substation
5 | Text Box | 3 | rob.urban | Split header box design
6 | Callout | 3 | rob.urban | To get a good distribution of liquid water through all tubes, it is a must to have only one tube layer per pass
7 | Callout | 3 | rob.urban | This drawing is not to be followed