## 019-E-DAT-00045-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Mohamed Ayyash | Typo, should read No.. to be applied to all sheets
2 | Callout | 1 | Mohamed Ayyash | Unit name missing. Add 2HCU, Apply to all sheets
3 | Callout | 1 | Mohamed Ayyash | Typo. delete c
4 | Typewritten Text | 1 | Mohamed Ayyash | General
5 | Typewritten Text | 1 | Mohamed Ayyash | comment:
6 | Typewritten Text | 1 | Mohamed Ayyash | Many text fonts throughout the document are too small and unreadable. Please enlarge
7 | Text Box | 1 | A.Jabbar Mahmood | General: TR to refer to MOC-JVD-LET-00001 Annex1 regarding changing the LT Naphtha Cutpoint from C5-65C to C5-180F for meeting the TVP limit. TR needs to check and confirm TPIT's findings and that no design change is required on this air cooler in terms of duty and design conditions.
8 | Callout | 2 | Mohamed Ayyash | Delete ";" in 3 locations marked with clouds (have no meaning)
9 | Callout | 2 | Adnan Alothman | Inlet Oper. Press. to be checked and confirm. As per FEED data sheet, it is 20.
10 | Text Box | 4 | A.Jabbar Mahmood | As discussed during th the P&IDs review sessions, TR to check the requirement for the sloping the air cooler bundles for the pressure control (as in the existing 1HCU) with CLG and accordingly cover this requirement in the datasheet
11 | Cloud+ | 4 | A.Jabbar Mahmood | What is this about? TR shall provide this document for owner's information and review.
12 | Cloud+ | 4 | A.Jabbar Mahmood | Spellout the word "Naphtha"
13 | Text Box | 4 | Hasan Asad | The Vendor/Supplier shall provide provision for extending the greasing ports to the platform level without the need of shutting down the fan and to reach the fan bearings ports for greasing. The Contractor shall include this requirement in the scope of supply for engineered solution.
14 | Text Box | 4 | Hasan Asad | The fans shall be equipped with anti-rotation mechanism.
15 | Call-out | 4 | Ahmed Marhoon | The scope for instrumentation and control is not limited to the alarms in DCS. All the control functions will be done in the DCS with the necessary interconnections with the electrical MCC. The final design of the system shall be based on the BMPS specifications (including relevant J class) and the final PID post detail design and Hazop3/SIL analysis. Suppliers to be instructed accordingly. This is a typical comment for all fin fan air coolers.
16 | Call-out | 4 | Mahdi Ali | Use Bapco number. FEED numbers shall not be used.