## 019-G-DAT-00001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | A.Jabbar Mahmood | Shall be changed to 019P0002A/B according to the new equipment numbering
2 | Text Box | 1 | Mahdi Ali | Unit number shall always be 3 digits
3 | Text Box | 1 | Mahdi Ali | Equipment code for motors is 'M'
4 | Callout | 1 | Mohamed Ayyash | NO. (Typo) correct on all pages
5 | Callout | 1 | Mohamed Ayyash | Should read 1/9 ( correct all pages)
6 | Text Box | 1 | A.Jabbar Mahmood | General to all pumps: Owner has not received the hydraulic calculations and hence cannot verify the revised pump head and design conditions.
7 | Call-out | 2 | A.Jabbar Mahmood | NPSHa is estimated by CLG as 227 ft (from top of foundation). Check and confirm
8 | Call-out | 2 | A.Jabbar Mahmood | Min CW inlet pressure at unit battery limit is 65 psig as per BMPS A1. Verify and confirm
9 | Call-out | 2 | A.Jabbar Mahmood | Min CW return pressure at unit battery limit is 36 psig per BMPS A1. Check and confirm
10 | Text Box | 3 | Hasan Asad | Dry Coupling
11 | Text Box | 3 | Hasan Asad | Min 7 in (180 cm) - Supplier to verify
12 | Callout | 4 | Isamu | TTSJV to add a remark "Vendor to consult seal vendor to employ plan 53B (with bladder) to avoid bubble formation by the pressurizing gas inside the seal pot"
13 | Cloud+ | 4 | Adnan Alothman | Mounting of Seal S. to be checked and verified according to the standard
14 | Text Box | 4 | Hasan Asad | Vendor/Supplier to provide stuffing box pressure for Owner use.
15 | Text Box | 5 | Hasan Asad | Yes
16 | Text Box | 5 | Hasan Asad | Yes
17 | Call-out | 7 | A.Jabbar Mahmood | What is the basis for the indicated max CW flow per pump?
18 | Call-out | 7 | A.Jabbar Mahmood | Higher than the pour point of the feed defined in the EDP (95 F). Does it include a safety margin? Check
19 | Cloud+ | 7 | A.Jabbar Mahmood | Flash point is 297 F as defined for the feed in the EDP
20 | Call-out | 7 | A.Jabbar Mahmood | This P&ID shall be included in the document or at least a sketch illustrating the warm-up system shown in the P&ID.
21 | Call-out | 7 | A.Jabbar Mahmood | A note shall be added indicating the warm-up medium (UCO), providing the main properties of UCO.
22 | Call-out | 7 | A.Jabbar Mahmood | Add to Note 24 "..and the warm up line isolation valve is left open by mistake"
23 | Call-out | 7 | A.Jabbar Mahmood | Add to Note 24 "..and the warm-up oil flowrate and temperature".
24 | Text Box | 7 | A.Jabbar Mahmood | A note to be added stating that the pump head may change as detailed design is developed.
25 | Cloud+ | 7 | bapco-user | 000-G-ITP-70001-001
26 | Callout | 7 | Isamu | Second page shows Normal flow rate. Please indicate rated flow rate if it means 115% of normal. The use of the world design shall be by Vendor only as per API 610 guidance
27 | Callout | 7 | Isamu | TTSJV shall indicate the maximum viscosity and specific gravity to count for motor sizing
28 | Text Box | 7 | Mahdi Ali | Bapco number to be referenced
29 | Call-out | 7 | Sameer Foujdar | Vendor to Specify the Operation of the the bypass lines on the spill-back valve and suction MOV
30 | Text Box | 7 | Hasan Asad | This needs to be verified by seal vendor capable for mechanical seal.
31 | Call-out | 8 | A.Jabbar Mahmood | correct the tag no.
32 | Text Box | 8 | Mahdi Ali | Equipment code for motors is 'M'
33 | Callout | 9 | Mohamed Ayyash | space