## 045-E-DAT-00003-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
3 | Cloud+ | Page 2 | Jawad Alawi | Refer to T1568 for tubes material
4 | Cloud+ | Page 2 | Sameer.Ahmed | This length is not as per BMPS-A1 8.2.3
5 | Callout | Page 2 | BD Mori | Specify the estimated highest temperature at transient operating conditions or upset scenario e.g start-up, shutdown, electrical power failure or any other operating scenario leading to the highest possible temperature expected at inlet to each air cooler. Based on the highest temperature if required the vendor shall perform FEA analysis.
6 | Text Box | Page 3 | Mahdi Ali | 3TGTU
7 | Text Box | Page 3 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
8 | Callout | Page 3 | Salman Jaffer | a) Please refer to Bid Query T1383 for the requirement for automatic louver b) Type 'B' manifold. c) The degree of the slop for free draining purpose per PIDs
9 | Callout | Page 3 | BD Mori | Do not use acronyms: Low Severity Wet H2S Service (LSS)
10 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3