## 046-E-DAT-00002-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
| Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
| Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
| Callout | Page 2 | balagangadhar.k | 2 bundles per bay is recommended. Check fan dia and fan/bundle ratio.
| Callout | Page 2 | balagangadhar.k | Duty is 11.08 MMBtu/hr, as per licensor datasheet
| Text Box | Page 3 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
| Callout | Page 3 | Salman Jaffer | a) Please refer to Bid Query T1383 for the requirement for automatic louver b) Type 'B' manifold. c) The degree of the slop for free draining purpose per PIDs
| Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3
| Callout | Page 3 | BD Mori | To be consistent with FEED data sheet add note : 046E4612 shall be identical to 047E4712 with heat duty of 11.08 MMBTU/Hr