## 048-E-DAT-00004-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
3 | Cloud+ | Page 2 | Sameer.Ahmed | As per BMPS-A1 8.2.3, O.D. 25.4 (1)
4 | Cloud+ | Page 2 | Sameer.Ahmed | Add note: Length to be as per BMPS-A1 8.2.3
5 | Callout | Page 2 | balagangadhar.k | Condensate is from a vessel operating at atmospheric pressure. Inlet Condensate temperature shall be saturation temperature at vessel operating pressure which is 212 F (refer vessel datasheet). Please change inlet temperature, duty & properties.
6 | Callout | Page 2 | BD Mori | As per PFD 212°F. Check and verify.
7 | Text Box | Page 3 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
8 | Callout | Page 3 | Salman Jaffer | Type 'D' manifold.
9 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3