## 058-A-BOD-50001-001-RA-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Add title in the header
2 | Call-out | Page 3 | Ali Hasan | replace the 'fuel gases' with the 'off gases'
3 | Call-out | Page 3 | Ali Hasan | replace 'fuels' with 'fuel gas'
4 | Call-out | Page 3 | Ali Hasan | Add No.2
5 | Call-out | Page 3 | Ali Hasan | Add '&' instead of comma
6 | Call-out | Page 3 | Ali Hasan | replace 'fuels' with 'fuel gas streams'
7 | Call-out | Page 3 | Ali Hasan | Add: CDUs, CGRU, GCU and others
8 | Call-out | Page 4 | Hasan Al Noaimi | Regeneration
9 | Call-out | Page 4 | Hasan Al Noaimi | Concentration
10 | Callout | Page 4 | Mohamed Ayyash | Hydro De-sulphurization Unit
11 | Callout | Page 4 | Mohamed Ayyash | Company
13 | Call-out | Page 4 | Ali Hasan | replace 'Treatments' with 'Treating'
15 | Call-out | Page 5 | Hasan Al Noaimi | From KGSP and Sulfinol Sysytem at No 1 Hydrogen Plant.
16 | Call-out | Page 5 | Hasan Al Noaimi | KGSP
17 | Callout | Page 5 | Mohamed Ayyash | Delete "the"
18 | Call-out | Page 5 | Ali Hasan | Modify Note 1: Fuel gas to the existing flares (Remote High Level, FCCU and LSFO flares) is supplied from the Khuff gas system.
19 | Call-out | Page 5 | Ali Hasan | Add Remote High Level flare
20 | Call-out | Page 5 | Ali Hasan | Modify Note 2: KGSP provides sweet gas to the pilot burners in LSFO heaters/incinerators and to other users. The sweet gas system can also be supplied from the Sulfinol Unit at No.1 Hydrogen Plant in the event of KGSP shutdown.
21 | Call-out | Page 5 | Ali Hasan | This is the existing fuel gas system, not post BMP. Please modify.
22 | Call-out | Page 5 | Ali Hasan | change to Note 2
23 | Call-out | Page 5 | Ali Hasan | note 2
24 | Callout | Page 6 | BD Mori | How about BMP SRUs for stat-up?
25 | Text Box | Page 6 | Mahdi Ali | The orientation of this page shall be be changed to landscape as per the BMPS-A8.
26 | Callout | Page 6 | Salman Jaffer | Residue Gas through 1&2 SGPs Amine Absorber (mixed with SGPs off Gas)
27 | Cloud+ | Page 6 | Sameer.Ahmed | Change "IMPOR" to "IMPORT"
28 | Call-out | Page 6 | Ali Hasan | Plant
29 | Call-out | Page 7 | Hasan Al Noaimi | and from 2/3 BAGRU
30 | Call-out | Page 7 | Hasan Al Noaimi | 3VDU
31 | Call-out | Page 7 | Hasan Al Noaimi | and RHLF Flare
32 | Call-out | Page 7 | Hasan Al Noaimi | N2 from the No1 Nitrogen Plant new unit
33 | Callout | Page 7 | Salman Jaffer | or (only one SGP on stream)
34 | Call-out | Page 7 | Ali Hasan | During HUB 1, fuel gas for sweeping 2&3 ARU flare header is provided from 1&2 SGP off gas as shown on PFD-50001-002 Note 11. Sweet khuff gas from 1BAGRU provides backup to sweeping the ARU flare header in case 1&2 SGP off gas is unavailable (refer to P&ID BRA-227276 Sht.1 of 2, Rev C). - Please modify this bullet basis the above comment. - The P&IDs, for fuel gas system, interconnecting and flare header within ARUs shall be updated in EPC to reflect the appropriate fuel gas arrangement.
35 | Call-out | Page 7 | Ali Hasan | Refer to fuel gas PFD 058-A-PFD-50001-002. During HUB 1, off gas from 1&2 SGP will be routed to No.1 0&11 Boilers, and backed-up by sweet gas from 1BAGRU. Please modify this bullet basis the above comment.
36 | Call-out | Page 7 | Ali Hasan | Add note: F7703 in 1HCU has a provision of firing rich gas from 1ARU
37 | Callout | Page 8 | Salman Jaffer | Exact locations of the new tie-ins on Alba and Riffa distribution points need to be finalized with GDN to make sure that no limitation on both distribution points. In case of there is limitation then scope of work has to be modified.
38 | Cloud+ | Page 8 | Sameer.Ahmed | Remove "As informed by BAPCO"
39 | Call-out | Page 8 | Ali Hasan | add 'the'
40 | Call-out | Page 8 | Ali Hasan | Add 'Currently'
41 | Call-out | Page 8 | Ali Hasan | change the pressure range: 800 to 850 psig
42 | Call-out | Page 8 | Ali Hasan | Add' new'
43 | Call-out | Page 8 | Ali Hasan | How about Spent Caustic treating unit thermal oxidiser?
44 | Call-out | Page 9 | Hasan Al Noaimi | Space to be provided for three commpressors 2 on line and one standby.
45 | Callout | Page 9 | Salman Jaffer | installation of compressors and associated facilities such as KODs, coalescer and coolers as required.
46 | Text Box | Page 9 | Edgardo | Refer to BMP-CON-LET-00038 regarding Khuff Gas Pressure at ALBA and RIFFA Distribution Points and space for future installation of compressors
47 | Call-out | Page 10 | Hasan Al Noaimi | This operation will continue post BMP. Bapco will continue to send ROG to BANAGAS
48 | Call-out | Page 10 | Hasan Al Noaimi | F7703
49 | Call-out | Page 10 | 986131 | Revisit and Correct the number based on revised SGP design.
50 | Cloud+ | Page 10 | Sameer.Ahmed | Remove" According to BAPCO instructions"
51 | Call-out | Page 10 | Ali Hasan | Add: Both procees gas systems will be interconnected.
52 | Call-out | Page 10 | Ali Hasan | SGP offgas firing in #2 H2 plant Reformer not to be pursue in EPC. Instead, the Contractor to review the feasibility of firing this gas in 6VDU heater, which has a provision for rich gas firing.
53 | Call-out | Page 10 | Ali Hasan | Please revise this para basis SGP Alternate 5 design. Normal case shall be ROG export to Banagas.
54 | Call-out | Page 11 | Hasan Al Noaimi | KGSP
55 | Text Box | Page 11 | Mahdi Ali | 38V0020
56 | Call-out | Page 11 | Ali Hasan | - Please refer to Fuel Gas system Hazop2 report, recommendation 29 for EPC action: Evaluate to provide additional source of sweet Khuff gas (e.g. 2BAGRU 3BAGRU) shall be provided to ensure continuous operation during HUB/shutdown when Sweet Khuff gas fro
57 | Call-out | Page 11 | Ali Hasan | - Please provide two separate bullets for sweet Khuff gas to No.10&11 Boilers and sweet gas to ARU flare header. - Refer to the comments on page 7 and modify as required.
58 | Note | Page 11 | Ali Hasan | Please add the following about KGSP in para 4.1.4: a) KGSP is designed for 3.2 MMSCFD. Typical sweet gas requirement: 2.30 MMSCFD (95 MSCFH) Maximum sweet gas requirement: 2.52 MMSCFD (105 MSCFH). b)Pressure requirement downstream of KGSP: Sweet gas pressure: Average sweet gas pressure to Awali: 450 psig. Average sweet gas pressure to tank farm: 85 psig . c)The design pressure is 550 psig at KGSP outlet.
59 | Call-out | Page 12 | 986131 | These numbers to be revised based on the revised SGP design.
60 | Call-out | Page 12 | 986131 | These numbers to be revised based on the revised SGP design. Both alternate and normal case of SGP design to be included.
61 | Call-out | Page 12 | 986131 | Fuel gas quality based on maximum possible diversion of 1HRU Off Gas Amine Absorber (C2301) outlet to be reviewed and added in the table.
62 | Call-out | Page 12 | Ali Hasan | 0.4Ib/MMSCF
63 | Call-out | Page 12 | Ali Hasan | Add table with expected process gas composition
64 | Call-out | Page 12 | Ali Hasan | TTSJV to advise the maximum residue gas that can be consumed in the heaters.
65 | Call-out | Page 12 | Ali Hasan | Range to be reviewed as part of SGP EPC work and should be on the basis of ROG export to Banagas.
66 | Call-out | Page 12 | Ali Hasan | The basis of 260 MMSCFD gas importing is not known. Please qualify with addational info.
67 | Call-out | Page 12 | Ali Hasan | Ensure the gas composition is consistence with 2&3BAGRU H&M balance
68 | Call-out | Page 12 | Ali Hasan | H2S content of 0.07 mole% shall be used as per BMPS-A1.
69 | Call-out | Page 13 | 986131 | These numbers to be revised based on the revised SGP design.
70 | Call-out | Page 13 | Ali Hasan | Please include the following in the fuel gas balance: 1. Review the case when ROG is distrubated to refinery fuel gas due to Banagas shutdown. 2. Develope the fuel gas balance for 1SGP train shutdown scenario.
71 | Call-out | Page 13 | Ali Hasan | Contractor shall evaluate all the SGP shutdown scenarios specified in Alternate 5 and ROG shutdown case. Develop all the possible cases before selecting the limiting case for burner. There will be more than 3 different composition.
72 | Call-out | Page 13 | Ali Hasan | As per the fuel gas meeting dated 13 April, a conservative number was to be used; 7Ib/MMSCF or 4degF?
73 | Call-out | Page 13 | Ali Hasan | Add 'mixing drum' for precise location
74 | Call-out | Page 14 | Hasan Al Noaimi | what about 380mbpd case.
75 | Callout | Page 14 | Salman Jaffer | Please include Platfromer Gas turbine.
76 | Cloud+ | Page 14 | Sameer.Ahmed | The total power generation from the existing gas turbines is more than 19 MW. The total rated power generation for the 3 gas turbines is 48MW (14.5 MW+14.5MW +19MW) The net power generation from the existing 3 Gas Turbines will not reduced considerably post BMP)
77 | Text Box | Page 14 | Khalid | Sameer Average MW = 34 based on P&U statistics Decommissioning Fcc, 1,2,3 cdu, vdus etc and transferring Awali to EWA power, assumption was made that new average = 30MW. Distributing 30 MW equally on 5 generators, each machine load = 6 MW. STGs load = 12 MW GTs load = 18 MW
78 | Call-out | Page 14 | Ali Hasan | Please provide estimated power generation for 380 MBPD case
79 | Text Box | Page 15 | Mahdi Ali | 022F0001A
80 | Text Box | Page 15 | Mahdi Ali | 007F0601A
81 | Text Box | Page 15 | Mahdi Ali | 070F0001
82 | Text Box | Page 15 | Mahdi Ali | 062F6200
83 | Text Box | Page 15 | Mahdi Ali | 063F6300
84 | Text Box | Page 15 | Mahdi Ali | 064F6402
85 | Text Box | Page 15 | Mahdi Ali | 077F7701
86 | Text Box | Page 15 | Mahdi Ali | 084F8401
87 | Text Box | Page 15 | Mahdi Ali | 078F7812
88 | Text Box | Page 15 | Mahdi Ali | 066F6605
89 | Text Box | Page 15 | Mahdi Ali | Follow the examples
90 | Callout | Page 15 | Salman Jaffer | 4A CDU uses both Residue gas and Process gas
91 | Cloud+ | Page 15 | Sameer.Ahmed | The net power generation post BMP from the existing 3 Gas Turbines will be more than 19 MW
92 | Call-out | Page 15 | Ali Hasan | General comment: New numbering/tagging shall be applied to the BMP heaters. Equipemnt tag for the existing heaters shall remains as is.
93 | Call-out | Page 15 | Ali Hasan | refer to the comments on page 14 about the 380 case.
94 | Call-out | Page 15 | Ali Hasan | Please include 470 duty for 4A CDU operating at design (104 MBPD)
95 | Call-out | Page 15 | Ali Hasan | Use 165
96 | Call-out | Page 15 | Ali Hasan | State weather this is an absorbed or fired duty. We assume it is fired. Please correct.
97 | Call-out | Page 15 | Ali Hasan | 24F1
98 | Call-out | Page 16 | 986131 | Update based on the Scope of work for SGP; Alternative Case 5 (BMP-CON-LET-00026)
99 | Call-out | Page 16 | Ali Hasan | Add Note 3: Bapco advised the following about Platformer/Unifiner off gases: 1. V5: Bapco has decided not to install Cl guard bed. This gas will be fired in the heater. 2. V20: this gas will also be fired in the heater. 3. V18: this gas will be fired in the heater. All 3 gases above are very rich in H2 and if routed to fuel gas drip drum, they will affect the combined fuel gas H2 content, whcih will affect the burner operation. Therefore, these gases will prefrentially fired in Platformer/Unifiner heater and only remaining gas will be routed to V1912/13. Unifiner/Platformer burners will be modified to fire 100% of this gas, however this modification is outside the BMP scope.
100 | Callout | Page 17 | Julio.Aguilar | Process gas to RHLF Flare to stack base and pilots to be added in this table
101 | Cloud+ | Page 17 | Julio.Aguilar | Equipment tag number to be revised as per the new numbering procedure and apply to all new BMP equipment throughout the whole document
102 | Callout | Page 17 | Fatema Hashem | WHAT IS THE BASIS OF THESE NUMBERS? THESE VALUES SHOULD REFLECT THE REQUIRED FIRED DUTY FOR 1RHCU HEATERS. CHECK AND CORRECT.
103 | Cloud+ | Page 17 | Sameer.Ahmed | Change to "10 & 11 HP Boilers"
104 | Callout | Page 17 | Sameer.Ahmed | 310F0001 311F0001
105 | Call-out | Page 17 | Ali Hasan | refer to the comments on page 14 about the 380 case.
106 | Call-out | Page 17 | Ali Hasan | Refer to the comment on page 15.
107 | Call-out | Page 17 | Ali Hasan | Please update the duties basis the EPC development
108 | Callout | Page 20 | Salman Jaffer | Liquid content in Khuff gas needs to be reviewed. As experienced in 1BAGRU, liquid accumulates upstream of the Amine Absorber.
109 | Callout | Page 20 | BD Mori | Repetition. Delete one of them
110 | Callout | Page 20 | BD Mori | Repetition. Delete one of them
111 | Callout | Page 20 | BD Mori | How this will be achieved in run with varying operating conditions? Will there be a calculation block?
112 | Call-out | Page 21 | Ali Hasan | Refer to the comment on page 7 about 2&3 ARU flare header.
113 | Callout | Page 21 | BD Mori | Repetition. Delete one of them
114 | Text Box | Page 23 | Julio.Aguilar | Considerer conditions in the battery limit for instrument air (minimum pressure) to be provided for the control valves to new M/S, Mixing and Sweet Khuff gas drums. In the M/S area the existing instrument air system shall be verified during project if is adequate to feed the new control valves.
115 | Call-out | Page 23 | Edgardo | This comment may not be applicable to this document and shall be considered in other applicable document