## 058-A-PFD-00002-001-R11A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Edgardo | Provide a note below the drawing number to read as follows: This document is copied from BRA-61289, which is now replaced with the new document number 058-A-PFD-00002-001
2 | Callout | 1 | Julio.Aguilar | Add: HP
3 | Callout | 1 | Julio.Aguilar | 1SGP
4 | Callout | 1 | Julio.Aguilar | 2SGP
5 | Callout | 1 | Julio.Aguilar | 2
6 | Cloud+ | 1 | Julio.Aguilar | Supplier
7 | Callout | 1 | Julio.Aguilar | Stream number 31 is currently with hold 1, however when the hold is removed the splitted streams will require a dedicated stream number as per BMPS-A8, page 90, numeral 2
8 | Callout | 1 | Julio.Aguilar | Consider inclusion of stream number for these streams
9 | Text Box | 1 | Mahdi Ali | Refer to general connects made on 010-A-PFD-00001-001 sent in transmittal BMP-MOC-TRI-00033
10 | Call-out | 1 | Ali Abbas | add tag no. based on 1000 series as agreed for brown field area
11 | Call-out | 1 | Ali Abbas | add arrow direction
12 | Call-out | 1 | Ali Hasan | Please refer to OWNER comments on Plant 058 design basis about routing Proces gas No.2 Plant. This option not to be persuade in EPC.
13 | Call-out | 1 | Ali Hasan | Add Note: Sulfinol Unit provides sweet gas to KGS users. Sweet gas can also be supplied from 1,2&3 BAGRU in the event of Sulfinol Unit shutdown
14 | Callout | 1 | Fatema Hashem | GENERAL COMMENT: USE "2H2P" NOT 2H2, "3H2P" NOT 3H2, "4H2P" NOT 4H2
15 | Call-out | 1 | Ali Hasan | Refer to BMPS-A1. Normal temperture is 65-75 degF. Max. is 150 degF. The system shall be capable of operating between min and max.