## 081-A-PFD-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Sameer.Ahmed | Include PFD numbers
2 | Call-out | 1 | Mahdi Ali | Since this is an existing unit then drawing number shall follow the existing number and additional sheets to be added. The existing drawing number is 081-A-PFD-00001-001, Therefore, those PFDs shall have the following numbers: 081-A-PFD-00001-002 & 081-A-PFD-00001-003
3 | Callout | 1 | Robert.Kawitzki | Equipment numbers as per project standards
4 | Callout | 1 | Robert.Kawitzki | Text height and width to project standard - typical comment
5 | Text Box | 1 | Mahdi Ali | Refer to general comments made on 010-A-PFD-00001-001 in transmittal BMP-MOC-TRI-00033
6 | Call-out | 1 | Mahdi Ali | Equipment data to be aligned below the equipment. Move to the right.
7 | Call-out | 1 | Ali Abbas | General: arrow direction
8 | Call-out | 1 | Ali Abbas | Missing tags
9 | Call-out | 1 | Ali Hasan | The FEED numbering/tagging system to be followed. The new numbering system in EPC is not applicable for Plant 81 (revamp unit). This is general comments applicable to all equipment in Plant 81.
10 | Call-out | 1 | Ali Hasan | Relief stream from Fuel Gas system to be included and considered within the total LSDP flare relief load. Refer to Owner response to T1424 and T603.
11 | Call-out | 1 | Ali Hasan | Note 4 is not clear. Is it applicable to the relief from No.10&11 Boilers, or the entire flare header?
12 | Callout | 1 | Syed Ahmed | please add additional note: At any time, only one of the SGP units (1SGP or 2SGP) and one of the ARU units (2ARU or 3ARU) can be lined up to LSDP Flare.