## 085-A-PFD-00001-002-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Sameer.Ahmed | Indicate the source PFD drawing number
2 | Callout | 1 | Mohamed Ayyash | As per BRA-227145 sheet 25, the mixer comes before the Control valve
3 | Call-out | 1 | Ali Abbas | Refer to applicable comments from sheet 1.
4 | Call-out | 1 | A.Jabbar Mahmood | Refer to the comment in sheet 1 on note 1.
5 | Call-out | 1 | A.Jabbar Mahmood | indicate the LC tag number i.e. the descriptor shall read "SIGNAL FROM LC0010"
6 | Cloud+ | 1 | A.Jabbar Mahmood | TITLE OF SHEET 2 SHALL READ " SECONDARY CALCITE BED PACKAGE"
7 | Call-out | 1 | A.Jabbar Mahmood | "...TO SECONDARY COOLING TOWER BASIN..."
8 | Call-out | 1 | 986131 | Review the drain location to CSS as the water is expected to have a very low pH (2). Ensure all the down stream equipment and piping are designed to handle the acidic water. Ensure it complies with the environmental regulations. Applied to all similar locations.
9 | Call-out | 1 | 986131 | break the secondary line - preferably the break to be in the vertical line as per BMPS A3.
10 | Call-out | 1 | 986131 | Move the line location so that it need not be broken.
11 | Call-out | 1 | Ahmed Marhoon | Outgoing stream description to indicate the destination of the stream.