## 085-A-PFD-00001-004-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Mahdi Ali | Refer to comments on sheet 3
2 | Callout | 1 | Mohamed Ayyash | 085BA0002
3 | Callout | 1 | Mohamed Ayyash | 085CWT0002
4 | Callout | 1 | Mohamed Ayyash | a missing signal line comes from the HC analyzer to this C/V
5 | Callout | 1 | Mohamed Ayyash | a missing signal line comes from the HC analyzer to this C/V
6 | Callout | 1 | Mohamed Ayyash | Add 085
7 | Callout | 1 | Mohamed Ayyash | add 085
8 | Callout | 1 | Mohamed Ayyash | Align
9 | Callout | 1 | Mohamed Ayyash | Align
10 | Call-out | 1 | A.Jabbar Mahmood | SHALL READ "SECONDARY COOLING TOWER BASIN"
11 | Call-out | 1 | A.Jabbar Mahmood | RATIO
12 | Cloud+ | 1 | A.Jabbar Mahmood | Keep the equipment no. at the end of the descriptor
13 | Cloud+ | 1 | A.Jabbar Mahmood | Spellout the full word
14 | Cloud+ | 1 | A.Jabbar Mahmood | The indicated pressure for these streams of 22 psig seems high, unless a pressure drop in the line downstream is 22 psi! Check and confirm
15 | Call-out | 1 | 986131 | refer note in sheet 3.
16 | Call-out | 1 | 986131 | Write Cl2 instead of Cl to indicate chlorine analyser.
17 | Call-out | 1 | 986131 | In P&ID this line is shown as a existing line - Correct the deception as necessary.
18 | Call-out | 1 | Ahmed Marhoon | Location of the FI to be corrected with reference to the AG/Bu.