## 085-A-PFD-00001-005-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Sameer.Ahmed | Indicate the PFD drawing number
2 | Callout | 1 | Mohamed Ayyash | Add 085
3 | Callout | 1 | Mohamed Ayyash | Add 085
4 | Call-out | 1 | Sameer Foujdar | Backwash system to be consistence with the P&ID for both Main and Secondary cooling water filter packages
5 | Call-out | 1 | A.Jabbar Mahmood | All eight filters shall be depicted with the associated instrementations
6 | Call-out | 1 | A.Jabbar Mahmood | All three filters shall be depicted with the associated instrementations
7 | Cloud+ | 1 | A.Jabbar Mahmood | delete
8 | Cloud+ | 1 | A.Jabbar Mahmood | delete
9 | Call-out | 1 | 986131 | The back wash line is sent to the BA0003 does not show a vent to safely remove the air during the back wash. Please study and address the design as required.
10 | Call-out | 1 | 986131 | Provide equipment number for the back wash blower and name plate details. The back wash line is sent to the BA0003 does not show a vent to safely remove the air during the back wash. Please study and address the design as required.
11 | Call-out | 1 | 986131 | What does MCF indicate? cover through a note if required.
12 | Cloud+ | 1 | 986131 | - Both the basins have the same number BA0003. consider providing A and B to distinguish the two. - The deception of Sump is different in P&ID and PFD. Show them in a manner such that it is easy to follow the process. - Show the Sluice gates and drains fr
13 | Call-out | 1 | 986131 | is it a normal practice to have a return line with RO to the sump? This would consume energy and the net output from the pump would be lower. Please critically review.
14 | Call-out | 1 | Sameer Foujdar | As per the process design basis backwash water flow is assumed to be double the capacity of the each bed filtration. Presently there is no means to measure the flow rate kindly advice.