## 085-E-DAT-00001-001-RAP-BB COM
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | Page 1 | Hasan Al Noaimi | Delete BMP
2 | Call-out | Page 1 | Hasan Al Noaimi
3 | Typewritten Text | Page 1 | Hasan Al Noaimi
4 | Typewritten Text | Page 1 | Hasan Al Noaimi
5 | Typewritten Text | Page 1 | Hasan Al Noaimi
6 | Rectangle | Page 1 | Hasan Al Noaimi
7 | Typewritten Text | Page 1 | Hasan Al Noaimi
8 | Typewritten Text | Page 1 | Hasan Al Noaimi | water
9 | Line | Page 1 | Mahdi Ali
10 | Text Box | Page 1 | Mahdi Ali | Follow official description
11 | Text Box | Page 1 | Ahmed Marhoon | No notes have been captured in this transmittal for the instrumentation & Control systems. TTSJV is requested to ensure that all the specific technical/functional requirements (including AVL) for the instrumentation and control scope are covered and detailed in the requisition specification that will be sent out to suppliers. Vendors to be notified on the fact that the final design of the system shall include all the Hazop/SIL (where the vendor will be involved) recommendation and approved PID. Also, a note to be added to this Data Sheet to emphasize on the requirement to comply with the project specifications and add a reference to the requisition specification. Since the Data Sheet is issued separately, the consistency between the different documents, that will be part of the requisition, could not be verified and hence it is the contractors responsibility to update the other documents impacted by any of the comments on this sheet and vice versa. Also applicable for 085-E-DAT-00002-001-RAP
12 | Text Box | Page 1 | 986131 | The following Bid Clarification effect the Water circulation rate (refer row 1 of data sheet) T251,T371,T372,T373 to T376,T579,T703,T810,T1544 Please ensure these are considered while recalculating the water circulation rate. In addition vendor data for package units are also likely to impact the final flow rate based on detailed engineering work.
13 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
14 | Stamp | Page 1 | mark.langerhorst
15 | Cloud+ | Page 2 | A.Jabbar Mahmood | It is 129772 gpm per FEED D/S. Check and confirm. Anyway, this number will need to be updated once the CW consumption in the user units has been finalized during EPC.
16 | Cloud+ | Page 2 | A.Jabbar Mahmood | 2715 gpm per FEED D/S. Check and confirm
17 | Cloud | Page 2 | Mahdi Ali
18 | Arrow | Page 2 | Mahdi Ali
19 | Callout | Page 2 | Mohamed Ayyash | Kingdom of
20 | Call-out | Page 2 | 986131 | Please re-check the evaporation loss (refer below caclulactions): Heat of water cooling = Mc Cp DT Wc =148821gpm Mc= 33460913.64kg/hr(density as 61.8 lb/ft3) Cp = 4.184 kJ / kg / °C DT = 12deg C Heat = 1680005552KJ/hr Water evaporated = heat/ Hv HV = 2260 kJ / kg We = 743365kg/hr = 3306gpm (5% higher than the figure shown)
21 | Callout | Page 2 | BD Mori | The exact CW consumption to be updated for BMP. Followed by that, update the CT BOD and its impact on Desal unit capacity. If necessary Desal unit BOD and capacity to be updated as required.
22 | Callout | Page 2 | Julio.Aguilar | Basis for Water circulation and evaporation losses figures shown in this Mechanical Process Data Sheet shall to be matched with unit u085 Process Design Basis and PFDs.
23 | Arrow | Page 2 | Julio.Aguilar
24 | Text Box | Page 3 | Antony.Bentley | Add min. concrete grade & BMPS reference
25 | Arrow | Page 3 | Antony.Bentley
26 | Arrow | Page 3 | Antony.Bentley
27 | Call-out | Page 3 | Hasan Al Noaimi | delete
28 | Callout | Page 3 | Mohamed Ayyash | Kingdom of
29 | Callout | Page 4 | bapco-user | As per BMPS-E8 point 6.10.1
30 | Line | Page 4 | Mahdi Ali
31 | Callout | Page 4 | Mohamed Ayyash | Kingdom of
32 | Callout | Page 5 | bapco-user | Drive Shaft: Austen SS or Carbon fiber composite
33 | Line | Page 5 | Mahdi Ali
34 | Callout | Page 5 | Mohamed Ayyash | Kingdom of
35 | Call-out | Page 6 | Hasan Al Noaimi | de
36 | Text Box | Page 6 | Ahmed Ali | in note 1, it said the normal circulation rate is 120497, second para normal rate to be confirmed later (contradiction). As per ITP normal consumption is 99831
37 | Callout | Page 6 | bapco-user | Note10: Typo error TDS: 184 ppm max
38 | Cloud+ | Page 6 | A.Jabbar Mahmood | Typo
39 | Cloud | Page 6 | Mohamed Ayyash
40 | Callout | Page 6 | Mohamed Ayyash | Is it Manufacturer? It is not standard
41 | Callout | Page 6 | Mohamed Ayyash | Water (add)
42 | Callout | Page 6 | Mohamed Ayyash | Water (add)
43 | Callout | Page 6 | Mohamed Ayyash | add space
44 | Callout | Page 6 | Mohamed Ayyash | be (add)
45 | Call-out | Page 6 | 986131 | Reconfirm the number based on evaporation loss figures.
46 | Cloud | Page 6 | 986131
47 | Call-out | Page 6 | 986131 | For clarity of note 9 & 10 please capture the entire explanation given in 2520-u085-CN0007-01B, section 2.2.
48 | Call-out | Page 6 | 986131 | Reconfirm the number based on evaporation loss calculation, drift loss and blow down.
49 | Text Box | Page 6 | Julio.Aguilar | Consider inclusion of a note saying:" Maximum allowed cooling water temperature from individual user at unit u085 inlet battery limit is 120 F."
50 | Callout | Page 6 | Julio.Aguilar | Please clarify Note 3 mentioning that that the wet bulb temp is 87F+1F
51 | Call-out | Page 6 | 986131 | Please include the contribution of TDS and chloride in the circulating water based on these chemical addition. In addition, provide contribution on TDS individually for each of the chemicals at the COC of design 7 and Normal 8.
52 | Text Box | Page 6 | Hasan Asad | Access for maintenance for motor & gearbox alignment purposes and for major overhaul.
53 | Call-out | Page 6 | Ali Abbas | Signal type to louvers shall be in line with instrumentation specifications BMPSs with position feedback to DCS and electronic positioner shall be compatible with fieldbus spec.
54 | Call-out | Page 6 | Ali Abbas | Motor status and other command where needed to DCS, per BMPSs.