## 085-G-DAT-00001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Isamu | Delete.
2 | Callout | 1 | Mohamed Ayyash | No. (Typo) apply to all document
3 | Text Box | 1 | A.Jabbar Mahmood | General: Decimal points shall be instead of commas as decimal separators
4 | Call-out | 1 | Ahmed Ali | General: the unit name to be changed to CWT
5 | Text Box | 1 | A.Jabbar Mahmood | General: The reported pump capacities and normal CW flowrates are not consistent with the design basis document, recently issued H&MB nor with the CWT datasheets. It is aslo understood that these numbers will be frozen at a later stage in the EPC once the CW consumptions for the users are finalized.
6 | Text Box | 1 | Hasan Asad | As per Volume 2 Exhibit 6 - CDRL - Complete LCCA study shall provided and recommendations shall be considered during design.
7 | Call-out | 2 | Mahdi Ali | Remove the space
8 | Call-out | 2 | A.Jabbar Mahmood | Add a note for the vendors stating the flow rates will change after the development of the detailed engineering and finalization of users CW consumption
9 | Cloud+ | 2 | A.Jabbar Mahmood | Ensure that the reported data, in particular and operating pressures, are consistent with BMPS A1
10 | Call-out | 2 | 986131 | Add: (note 31)
11 | Cloud+ | 2 | 986131 | data changed from FEED - Detail engineering work explaining the change to be submitted for Owner's review.
12 | Call-out | 2 | 986131 | Provide the NPSHa considering that the water is saturated with dissolved air. The revised NPSHa is expected to be low (liquid head above the pump suction minus the friction loss). To avoid a over conservative pump design indicate the Effective NPSHa, calculated at the pump suction pressure when the volume of the flashed gas is 2% (or lower figure if the dissolved gas is less) the total volume. Cover this through notes - as a example extract from a existing refinery pump is attached for your reference.
13 | Text Box | 4 | Hasan Asad | This shall be verified during detailed design as the sealing system shall not obstruct any other maintenance activity such as pump removal, surveillance.
14 | Text Box | 4 | Hasan Asad | As per BMPS A3, this shall be 3
15 | Text Box | 5 | Hasan Asad | WIT
16 | Text Box | 5 | Hasan Asad | YES
17 | Call-out | 6 | Jawad Alawi | Typical: Specify the refered to standard
18 | Text Box | 6 | Ahmed Marhoon | The following are general comments related to instrumentation and control: 1. The notes related to Instrumentation & Control provided on the Data Sheet do not capture all the technical requirements for the instruments design. All applicable BMPS-J series to be referenced (such as J2, J3, J18 &etc) for the supplier to comply with. 2. TTSJV is requested to ensure that all the specific technical/functional requirements (including AVL) are covered and detailed in the requisition specification that will be sent out to suppliers. In case this document would be the only one for MR, then all the relevant BMPS to be included in the Data Sheet notes. 3. Vendors to be notified on the fact that the final design of the system shall include all the Hazop3/SIL recommendations and approved PID post-EPC-development. 4. Since the Data Sheet is issued separately, the consistency between the different documents, that may be part of the requisition, could not be verified and hence it is the contractors responsibility to update the other documents impacted by any of the comments on this Data Sheet and vice versa. 5. Minimum Flow arrangement/design shall be reviewed and confirmed by the supplier. 6. Supplier to be notified on the requirements of the sequence operation, trip, autostart, permissive and other functional specification covered on the PID. 7. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. 8. Requirement of MCM to be verified with the supplier. Reference to BMPS-J15 MCM to be added accordingly. 9. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 10. All the machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 11. Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 12. Assistance and involvement of the vendor during CHAZOP/Hazop workshops and study to be considered. 13. Explanatory notes to be added on the requirement of having the control performed in the plant DCS and safety functions in ESD system. 14. Scope of supply for the interposing relays to be clearly defined. 15. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 16. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting &etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31.
19 | Text Box | 7 | Sankara | Delete Ex p
20 | Call-out | 7 | Mahdi Ali | Remove 'u' from Unit number
21 | Callout | 7 | Mohamed Ayyash | This is a Motor
22 | Callout | 8 | Mohamed Ayyash | Align
23 | Cloud+ | 8 | 986131 | Ensure that all notes in this data sheet have a unique number to avoid confusion.
24 | Callout | 9 | Mohamed Ayyash | Correct
25 | Callout | 9 | Mohamed Ayyash | Why write outside the table ?
26 | Call-out | 9 | Ahmed Ali | change to CWT
27 | Cloud+ | 9 | 986131 | Ensure all note in this drawing has a unique number. Example note 1,2 & 4 on page 19 has no relavence to these notes.
28 | Text Box | 13 | Hasan Asad | AVL Only
29 | Text Box | 15 | Hasan Asad | Mechanical Trip
30 | Callout | 16 | Mohamed Ayyash | Overlapping (Correct)
31 | Text Box | 16 | Hasan Asad | To be verified basis Vendor design
32 | Text Box | 17 | Hasan Asad | Electronic and Mechanical Trip
33 | Text Box | 17 | Hasan Asad | YES and Witness
34 | Text Box | 17 | Hasan Asad | Yes
35 | Text Box | 17 | Hasan Asad | Spare rotor to be tested.
36 | Text Box | 18 | Hasan Asad | 9) LCCA for 20 years to be provided by the Vendor for similar model.
37 | Call-out | 18 | 986131 | These note have same number as notes in page 19. provide unique number for all notes in this data sheet.
38 | Call-out | 19 | Mahdi Ali | Use Bapco number
39 | Text Box | 19 | Hasan Asad | Seal API plan shall be accessible for seal pot filling.
40 | Call-out | 19 | A.Jabbar Mahmood | As per the design basis document, the flowrates to the side filters and the blowdown shall be remain the same as in the senario of unavailability of BMP Secondary Cooling Water System
41 | Call-out | 19 | A.Jabbar Mahmood | Ensure that this is inline with BMPS A1
42 | Text Box | 19 | 986131 | 31 The source of Cooling water is direct contact cooling tower and the water is saturated with air: Composition: Water: xx mole%, Air: yy mole%. (Contractor to fill the mole composition of water and air)
43 | Call-out | 19 | 986131 | NPSH test is required and not conditional. if additional NPSH test for lower than 1m - like API clause 8.3.4.3.3 or 8.3.3.6 - is required - then clearly specify.