## 085-S-DAT-00012-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Isamu | Content indicates specifications. Please consider rewording of this title. Applicable to all documents in this transmittal
2 | Call-out | 1 | MAK | COOLING WATER TOWER OR CWT for short form. This change shall be reflected globally.
3 | Text Box | 1 | MAK | The correct document template (cover page and format) shall be used. MOC shall coordinate with the Directorate for the correct template.
4 | Text Box | 1 | Raj | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3.
5 | Text Box | 3 | Sankara | automation?
6 | Call-out | 3 | Ali Abbas | Please note that package units shall be controlled/protected from SRR DCS/ESD/MCM etc. equipment and avoid local PLC or other control system where ever is possible which is inline with our specification for package unit BMPS-J6. Unless there is a technical reasons that this package can't be controlled from the DCS in which Owner need to review/comment/approve any deviation from our specification.
7 | Text Box | 4 | Ahmed Marhoon | The following are comments related to instrumentation and control. These comments are also applicable for 085-S-DAT-00013 issued as part of this Transmittal. 1. Instruct the supplier to source instrumentations from project AVL only. 2. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this document shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 3. TTSJV is requested to ensure that all the specific technical/functional requirements are covered and detailed in the requisition specification that will be sent out to suppliers. In case this document would be the only one for MR, then all the relevant BMPS to be included in the Data Sheet notes. 4. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 5.Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 6. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting &etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 7. In addition to BMPS-J6, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J2, J3, J15 ... etc. All instruments and control systems to be designed according to BMPS specifications. 8. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 9. Supplier to comply with all the applicable BMPSs and provide, as a minimum, all the documents, hardware, software and services according to the relevant sections of the BMPSs in the agreed standard formats of the project. List to reflect all the required deliverables in accordance to BMPS J series. 10. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval.
8 | Call-out | 5 | Hasan Al Noaimi | FED
9 | Call-out | 6 | Ahmed Marhoon | How will the local control be achieved? The current revision of PID does not indicate this requirement. Will a local hand switch be provided at the field? or the idea is to have a manual reset on the solenoid valves? Also, what are the safety measures that will be in place during the manual control/sequence mode? The control system design shall be capable of allowing this operation and ensure a Bumpless transfer design is in place.
10 | Cloud+ | 7 | A.Jabbar Mahmood | Clarify why two filters?
11 | Cloud+ | 7 | A.Jabbar Mahmood | As per the H&MB data, the design flow rate is 325 USgpm and normal flow is 188 USgpm. Check, confirm and update documents (PFD, P&IDs, etc) accordingly
12 | Callout | 7 | alexis.martinez | GENERAL: use in the entire document the word "Manufacturer" instead of "MFR". Correct the document accordingly.
13 | Callout | 7 | alexis.martinez | In the section 3.3, second and 11th point of process requirements list, add "see table 3.1 in section 3.4".
14 | Callout | 7 | alexis.martinez | In the section 3.3, 5th and 10th point of process requirements list, replace the symbol "@" by "at the"
15 | Callout | 7 | alexis.martinez | In the section 3.3, 5th and 10th point of process requirements list, replace the symbol "@" by "at the"
16 | Call-out | 7 | 986131 | Add: Per filter
17 | Text Box | 8 | Sankara | BMPS-P2 delas with area classification
18 | Call-out | 8 | A.Jabbar Mahmood | Guarantees on the minimum time between filter reloads shall be provided.
19 | Call-out | 9 | Ebrahim | and General Design Rules for Electrical System, BMPS-P1
20 | Text Box | 10 | Ahmed Ali | * The requirement and the procedure for calcite filling
21 | Text Box | 10 | A.Jabbar Mahmood | General: Filters and Calcite beds are being used interchangeably for the same item. Consistency shall be applied
22 | Call-out | 10 | A.Jabbar Mahmood | and easy access for filter reloading.
23 | Call-out | 10 | Ahmed Marhoon | Mixing of electrical and instrument component/signals is against the BMPS standard. HV electrical equipment shall be completely segregated from the LV control equipment. Junction boxes dedicated for instrumentation shall be designed and supplied in compliance with the BMPS specifications. This bullet to be amended accordingly.
24 | Call-out | 10 | Ahmed Marhoon | Documents supplied by the supplier/contractor shall be developed based on the owner standard formats provided for the project. Simplified version is not acceptable.
25 | Call-out | 10 | Ahmed Marhoon | Should "interlock" be replaced with "sequence"?
26 | Call-out | 10 | 986131 | Access for removing and replacement of the bed. including any dump nozzles that may be requried.
27 | Call-out | 10 | 986131 | calcite bed maintenance procedure - Provide procedure of unloading and loading the calcite media. Method statement to safely dispose the discarded media to be provided in accordance with the local law.
28 | Call-out | 10 | 986131 | Effluent generated, Including any sold waste that may be generated during bed replacement.
29 | Callout | 10 | alexis.martinez | In page 10, section 4, add "maintenance manuals" on point 17th.
30 | Call-out | 10 | 986131 | Consider providing platform for safe and ease of bed replacement.
31 | Call-out | 11 | 986131 | Add: Note 3 (for consistency with section 3.3)
32 | Call-out | 12 | Ahmed Marhoon | The table included does not cover all the piping material classes requirements. For instance, the material class and thickness of impulse tubing is not mentioned. According to BMPS-J2/J6, SS316 is to be considered for the instrument impulse tubing. In addition to the table, a reference to the applicable BMPS standard to be added in order to capture all the specifications requirements. This is a typical comment for similar sections on all transmittals where only a portion of the BMPS specification is extracted and included in the materials specifications.
33 | Callout | 12 | Yousif Ahmadi | Piping classes to be checked and confirmed considering low pH
34 | Call-out | 13 | MAK | General Comment: Bapco's Document/Drawing numbers shall be used for all references.
35 | Text Box | 13 | Mahdi Ali | (FEED numbers shall not be used)