## 085-S-DAT-00015-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | MAK | COOLING WATER TOWER OR CWT for short form. This change shall be reflected globally.
2 | Text Box | 1 | MAK | The correct document template (cover page and format) shall be used. MOC shall coordinate with the Directorate for the correct template.
3 | Cloud+ | 5 | A.Jabbar Mahmood | Clarify the statement.
4 | Cloud+ | 5 | A.Jabbar Mahmood | Clarify this statement.
5 | Text Box | 6 | Mahdi Ali | Equipment tag is not as per BMPS-A8
6 | Call-out | 6 | A.Jabbar Mahmood | As per the PFD, the basin is numbered as 085BA0002. Check and update
7 | Call-out | 6 | Ahmed Marhoon | How will the local control be achieved? The current revision of PID does not indicate this requirement. Will a local hand switch be provided at the field? or the idea is to have a manual reset on the solenoid valves? Also, what are the safety measures that will be in place during the manual control/sequence mode? The control system design shall be capable of allowing this operation and ensure a Bumpless transfer design is in place.
8 | Cloud+ | 7 | A.Jabbar Mahmood | As per the H&MB data, the design flow rate is 4000 USgpm. Check, confirm and update documents (PFD, P&IDs, etc) accordingly
9 | Cloud+ | 7 | A.Jabbar Mahmood | Advise the basis of the max allowable pressure drop of 36 psi.
10 | Cloud+ | 7 | A.Jabbar Mahmood | As per the PFD, the pressure at the inlet of the flow control valve is 76 psig. Accordingly the pressure at the inlet of the filter is expected to be less than 76 psig. Check and update accordingly the appropriate documents.
11 | Call-out | 7 | 986131 | Add: "per filter"
12 | Text Box | 8 | Sankara | P2
13 | Call-out | 8 | A.Jabbar Mahmood | The targetted TSS at the outlet of each filter shall be specified and guaranteed.
14 | Cloud+ | 8 | 986131 | Review the TDS and Chloride based on the chemical dosing to the cooling tower and update.
15 | Call-out | 8 | 986131 | Add in 3.5.: - Maximum pressure drop at normal water flow expected after backwash - Minimum operating time for the filter. - If the filter media is replaceable cartage then life of filter to be guaranteed.
16 | Call-out | 9 | Ebrahim | and General Design Rules for Electrical System, BMPS-P1
17 | Text Box | 10 | Mahdi Ali | Layout
18 | Call-out | 10 | Sameer Foujdar | Secondary cooling water side stream filters are three not eight.
19 | Call-out | 10 | Ahmed Marhoon | Mixing of electrical and instrument component/signals is against the BMPS standard. HV electrical equipment shall be completely segregated from the LV control equipment. Junction boxes dedicated for instrumentation shall be designed and supplied in compliance with the BMPS specifications. This bullet to be amended accordingly.
20 | Call-out | 10 | 986131 | access for removing and replacement of filter element / media. If a media is used then proper dump nozzles to be provided.
21 | Call-out | 10 | 986131 | Filter maintenance procedure - In case of cartage - provide replacement method. Method to dispose the cartage in accordance with the local environmental law to be provided. And if acid cleaning of other methods are to be employed provide the details. In case of media - provide procedure of unloading and loading the filter media. Method statement to safely dispose the media to be provided in accordance with the local law. Note: In case special cleaning procedure are to be employed (say acid cleaning etc.) adequate arrangement to be made to facilitate the same.
22 | Call-out | 10 | 986131 | Effluent generated, Including any sold waste that may be generated during bed/ cartage replacement.
23 | Call-out | 10 | 986131 | Consider providing platform for safe and ease of filter cartage/filter media replacement.
24 | Call-out | 13 | MAK | General Comment: Bapco's Document/Drawing numbers shall be used for all references.