## 087-A-PFD-00001-002-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Sameer.Ahmed | Equipment tag number to be updated as per BMPS A8
2 | Text Box | 1 | MAK | Refer to Sht. 001 for the General Comments.
3 | Callout | 1 | Salman Jaffer | There is discrepancy between stream No.1 of this document and the source. Per this document, Normal Volumetric rate is (182 US gpm) as follows: (112 US gpm) from BMP main CW Blowdown plus (70 US gpm) from BMP Secondary CW Blowdown. But if you refer to streams No.15 and 21 of BMP CW (085) PFD BRB-228966 rev0 sheets 9&10 of 13, it shows: (112 US gpm) from BMP main CW Blowdown plus (4 US gpm) from BMP Secondary CW Blowdown. Please review this discrepancy, which one is correct?
4 | Text Box | 1 | Sameer.Ahmed | This drawing is given CODE-2 as a special case to allow TTSJV to proceed with development of subsequence deliverables and procurement activities. However, TTSJV shall be responsible to incorporate the comments and complete the design before finalizing the equipment PO. TTSJV to advise when the first utilities balance will be submitted for review. PFD shall be modified to incorporate the updated utilities streams data and H&M balance.