## 310-A-PFD-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Julio.Aguilar | Add: arrow here
2 | Text Box | 1 | MAK | Align the Equipment Data Blocks with the equipment symbols where possible.
3 | Call-out | 1 | MAK | Always show the border size A1
4 | Text Box | 1 | Julio.Aguilar | Equipments inside the package to be tagged as per BMPS-A8 once vendor package information is available.
5 | Callout | 1 | Julio.Aguilar | Include HP boiler capacity and design pressure as per BMPS-A8
6 | Text Box | 1 | MAK | Move a bit and align it
7 | Text Box | 1 | MAK | Move to here
8 | Cloud+ | 1 | Julio.Aguilar | Please clarify what is this instrument/valve and it is to be shown on symbology BMPS-A-50003.
9 | Call-out | 1 | Edgardo | Please indicate the BL per BMPS-A-50003; these lines are connected to different units; this comment applies for all lines which are connected to different units
10 | Callout | 1 | Julio.Aguilar | Please show in dotted line-type the inlet device as is mentioned in the BMPS-A8
11 | Cloud+ | 1 | Julio.Aguilar | Please, to be consistent with BMP process units modify the arrow description to indicate "SCALE CORROSION INHIBITOR FROM SCALE CORROSION INHIBITOR DOSING PACKAGE (310U0001)"
12 | Cloud+ | 1 | Sameer.Ahmed | Refer to HP Boiler 311 comment regarding the analyzer (O2 & combustible analyzer)
13 | Call-out | 1 | Mahdi Ali | Scale: NTS
14 | Callout | 1 | Julio.Aguilar | Source PFD number to be revised.
15 | Call-out | 1 | Ali Abbas | state signal from which instrument tag no.
16 | Text Box | 1 | Sameer.Ahmed | This drawing is given CODE-2 as a special case to allow TTSJV to proceed with development of subsequence deliverables and procurement activities. However, TTSJV shall be responsible to incorporate the comments and complete the design before finalizing the equipment PO. TTSJV to advise when the first utilities balance will be submitted for review. PFD shall be modified to incorporate the updated utilities streams data and H&M balance.
17 | Call-out | 1 | MAK | Total Sht. shall be indicated only, 004
18 | Callout | 1 | Sameer.Ahmed | Unit number shall be without the prefix "u" (this comment applies for all plant number mentioned in this drawing)
19 | Text Box | 1 | MAK | Use the latest PFD border template that is part of Homogenization Procedure. SOC shall coordinate with JV Directorate.