## 382-A-PFD-00001-002-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Sameer.Ahmed | This drawing is given CODE-2 as a special case to allow TTSJV to proceed with development of subsequence deliverables and procurement activities. However, TTSJV shall be responsible to incorporate the comments and complete the design before finalizing the equipment PO. TTSJV to advise when the first utilities balance will be submitted for review. PFD shall be modified to incorporate the updated utilities streams data and H&M balance.
2 | Call-out | 1 | Ali Abbas | Change to LC
3 | Callout | 1 | Julio.Aguilar | PFD number corresponding to the existing sewage treatment plant (STP) shall be assigned here for the final destination of the sanitary water from BMP.
4 | Cloud+ | 1 | Sameer.Ahmed | Show capacity and dimensions as per BMPS-A8, section 7.2.6
5 | Cloud+ | 1 | Julio.Aguilar | These streams collect Sanitary water from the new BMP units so a collecting drawing have to be developed in further stage showing all units streams and the assignation of a drawing number shall be provided.