## 000-F-GRD-80001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud |  | Edgardo
2 | Call-out |  | Edgardo | Please confirm the Unit number; If this steam reformer is part of the Hydrogen Plant, note that the hydrogen plants have their own assigned unit number
3 | Callout |  | BD Mori
4 | Callout |  | BD Mori
5 | Call-out |  | Ahmed Marhoon | The following are general comments related to instrumentation and control. All relevant sections of this transmittal to be updated accordingly (including the data sheets and SOW). 1. In addition to BMPS-J6, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J3, J9 ... etc. All instruments and control systems to be designed according to BMPS specifications. 2. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. 3. Add a note on the nozzle location for PEMS/CEMS to be coordinated/finalized with the PEMS/CEMS vendor. 4. The way the exclusion list is stated in this document results in misunderstandings and leads to unclear SOW. e.g. BMS Hardware Vs. Instrumentation Line of SOW document of this Transmittal. 5. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS for the ID fans in addition to vendor requirement. 6. Supplier to be instructed to source all instrumentation from the approved AVL for BMP. 7. List of documents, hardware, software and services to comply with the BMPS specifications (including tests and certifications). 8. Reference to BMPS-J10 Wireless to be added. Supplier to be notified on the criteria being development for instruments that can be accepted as wireless for non-critical measurement. 9. Scope of supply of Analyzers could not been found in this Transmittal. To be clarified 10. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Details listed below shall be firmed based on the approved PID and post Hazop3/SIL studies.
6 | Stamp |  | Nalini Mohan
7 | Text Box |  | Nalini Mohan | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3
8 | Call-out |  | Ali Abbas
9 | Call-out |  | Ali Abbas | Also, access ladder and platform to the PEMS-CEMS Nozzle to be provided.
10 | Call-out |  | Ali Abbas | MCM probes to be fitted by machinery vendor meeting spec.
11 | Callout |  | Mohamed Ayyash | add . (dot)
12 | Arrow |  | Mohamed Ayyash
13 | Arrow |  | Mohamed Ayyash
14 | Arrow |  | Mohamed Ayyash
15 | Arrow |  | Mohamed Ayyash
16 | Callout |  | Mohamed Ayyash | change to ; to .
17 | Call-out |  | Ali Abbas | ESD and
18 | Call-out |  | Ahmed Marhoon | Add CHAZOP
19 | Cloud |  | Ahmed Marhoon
20 | Call-out |  | Ahmed Marhoon | These activities are major milestones for the package and it is mandatory to be attended by Client representatives. Attendees list to be updated based on the agreed project matrix.
21 | Call-out |  | Ahmed Marhoon | Correct abbreviation is ESD.
22 | Call-out |  | Ahmed Marhoon | This is an IFAT and not loop test
23 | Call-out |  | Ahmed Marhoon | What about SAT?
24 | Call-out |  | Ahmed Marhoon | These notes to be added on all MRs issued for the project.
25 | Callout |  | Mohamed Ayyash | No.
26 | Callout |  | Syed Ahmed | Provision for shell side cleaning if necessary.
27 | Callout |  | Syed Ahmed | Provision for gas sampling and checking draft pressure is required for effective startup and operation of the
28 | Callout |  | Mohamed Ayyash | No.
29 | Call-out |  | Ahmed Marhoon | What about equipment requiring fireproofing per the FEE classification and being supplied by vendor?
30 | Call-out |  | Ahmed Marhoon | Refer to the applicable BMPS specifications such as BMPS A3, J2, J3, J6 ... etc.
31 | Call-out |  | Ahmed Marhoon | Add the necessary notes on the DCS, BMS (ESD), emission monitoring and MCM requirements based on BMPS-J series and BMPS-A3 specifications.
32 | Call-out |  | Ahmed Marhoon | A comprehensive list of exclusions to be added to the MR. e.g. What does BMS Hardware refer to? ESD system or even the field instruments?
33 | Arrow |  | Ahmed Marhoon
34 | Callout |  | Mohamed Ayyash | remove :
35 | Call-out |  | Ahmed Marhoon | To be detailed in accordance with on BMPS-J series specifications such as J2 and J6.
36 | Call-out |  | Ahmed Marhoon | Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement for the ID and FD fans
37 | Callout |  | Mohamed Ayyash | space
38 | Callout |  | Mohamed Ayyash | Don't use justify, use tab to align for better appearance
39 | Arrow |  | Mohamed Ayyash
40 | Arrow |  | Mohamed Ayyash
41 | Arrow |  | Mohamed Ayyash
42 | Arrow |  | Mohamed Ayyash
43 | Arrow |  | Mohamed Ayyash
44 | Call-out |  | Ahmed Marhoon | For instrumentation automation, supplier to be referred to the Standards and Codes of BMPS-J series
45 | Callout |  | Mohamed Ayyash | Don't use justify, use tab to align for better appearance
46 | Arrow |  | Mohamed Ayyash
47 | Arrow |  | Mohamed Ayyash
48 | Arrow |  | Mohamed Ayyash
49 | Callout |  | Mohamed Ayyash | space
50 | Callout |  | Mohamed Ayyash | add -
51 | Call-out |  | Ahmed Marhoon | Add a note to clarify the scope of supply of ESD
52 | Call-out |  | Ahmed Marhoon | Add a note to clarify the scope of supply of DCS.
53 | Call-out |  | Ahmed Marhoon | Add other BMPS specs such as J2, J3, J7, J9 ...etc.
54 | Callout |  | BD Mori | Vendor shall provide air sleeves around the tube inlet to the reformer and outlet from the reformer to prevent air ingress from the gaps into the radiant box.
55 | Callout |  | Syed Ahmed | In all levels.
56 | Callout |  | BD Mori | Vendor shall consider removal of burner in service for maintenance and cleaning in run. Therefore provide required space at reformer top for removal of the burner while unit is in operation.
57 | Callout |  | Syed Ahmed | Field pull button for emergency trip at top and ground level.
58 | Callout |  | Nalini Mohan | Owner's response on query T786 shall be followed for design of platform, walkways. The proposed widths are not acceptable
59 | Call-out |  | Ahmed Marhoon | Add requirements of MCM
60 | Call-out |  | Ahmed Marhoon | Add "or latest"
61 | Callout |  | BD Mori | Stack sample line shall be extended to ground level for periodic stack sampling
62 | Callout |  | Mohamed Ayyash | space
63 | Callout |  | Syed Ahmed | with two mobile optical pyrometers for startup .
64 | Callout |  | Mohamed Ayyash | add - and align