## 000-F-GRD-80002-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out |  | Ahmed Marhoon | The following are general comments related to instrumentation and control. All relevant sections of this transmittal to be updated accordingly. 1. In addition to BMPS-J6, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J3, J9 ... etc. All instruments and control systems to be designed according to BMPS specifications. 2. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. 3. Supplier to be instructed to source all instrumentation from the approved AVL for BMP. 4. List of documents, hardware, software and services to comply with the BMPS specifications (including tests and certifications). 5. Compliance to licensors mandatory and recommended requirements to be included. 6. It is noticed that there is limited scope for instrumentation and automation in this Transmittal. A clear interface plan to be developed to clearly describe the scope of supplier and contractor. 7. Supplier to be notified on possible changes to the current design after detail design development and Hazop3/SIL studies. Equipment shall be designed in accordance with the EPC approved PID. 8. Necessary notes to be added on the requirement of having the control on DCS and the BMS on ESD systems.
2 | Stamp |  | Nalini Mohan
3 | Text Box |  | Nalini Mohan | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3.
4 | Callout |  | Nalini Mohan | Combustion chamber design should incorporate flexibility to install different types of burners from Licensors approved list (included with ITB AVL)
5 | Callout |  | BD Mori | Reaction Furnace Burner vendor shall be selected and finalised in consultation with and approval of Bapco.
6 | Arrow |  | BD Mori
7 | Arrow |  | BD Mori
8 | Callout |  | Saeed Taher | Refractory lining shall be cured and dried out as per manufacrturer's recommendations as per BMPS-F6
9 | Callout |  | BD Mori | Furnace/Burner vendor to carry out CFD modeling as specified in the data sheet
10 | Callout |  | Syed Ahmed | Startup thermocouple for low temperature during startup and shutdown time.
11 | Arrow |  | Jeung.Kim
12 | Text Box |  | Jeung.Kim | Typical comment for all shop installed refractories: How to ensure any possible damage of the refractory during transportation?
13 | Callout |  | Nalini Mohan | suggest to increase to 10%
14 | Callout |  | Nalini Mohan | Are these spares for equipment related to 3 units 041/042/043?
15 | Line |  | Mohamed Ayyash
16 | Line |  | Mohamed Ayyash
17 | Line |  | Mohamed Ayyash
18 | Line |  | Mohamed Ayyash
19 | Line |  | Mohamed Ayyash
20 | Line |  | Mohamed Ayyash
21 | Line |  | Mohamed Ayyash
22 | Typewritten Text |  | Mohamed Ayyash | .
23 | Typewritten Text |  | Mohamed Ayyash | .
24 | Typewritten Text |  | Mohamed Ayyash | .
25 | Typewritten Text |  | Mohamed Ayyash | .
26 | Typewritten Text |  | Mohamed Ayyash
27 | Typewritten Text |  | Mohamed Ayyash | .
28 | Typewritten Text |  | Mohamed Ayyash | .
29 | Typewritten Text |  | Mohamed Ayyash | .
30 | Typewritten Text |  | Mohamed Ayyash | .
31 | Callout |  | Mohamed Ayyash | Add ,
32 | Callout |  | Nalini Mohan | Include reaction furnace burner as per the AVL in the sub-supplier list
33 | Callout |  | Mohamed Ayyash | space
34 | Line |  | Mohamed Ayyash
35 | Line |  | Mohamed Ayyash
36 | Typewritten Text |  | Mohamed Ayyash | .
37 | Typewritten Text |  | Mohamed Ayyash | .
38 | Callout |  | Mohamed Ayyash | , commissioning
39 | Callout |  | Mohamed Ayyash | space
40 | Callout |  | Mohamed Ayyash | , start up