## 000-F-GRD-80004-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box |  | Sameer.Ahmed | No. 10 HP Boiler & No. 11 HP Boiler
2 | Call-out |  | Ahmed Marhoon | Data sheets and other documents of this Transmittal shall be update based on the comments indicated on this document to ensure consistency.
3 | Cloud+ |  | Sameer.Ahmed | Replace "Auxiliary" with "HP" throughout all documents
4 | Stamp |  | Nalini Mohan
5 | Text Box |  | Nalini Mohan | This transmittal is reviewed with Status Code-3. This stamp is applicable to all the documents within this transmittal.
6 | Text Box |  | Jeung.Kim | Is this document a separate deliverable or part of the MR? Contractor has to clearly indicate it as Contractor only proposed to review the MDS and MR review in the same time during KOM.
7 | Callout |  | Mohamed Ayyash | why big gap? adjust on all headings and sub headings. By doing so the number of pages will be reduced
8 | Arrow |  | Mohamed Ayyash
9 | Callout |  | Mohamed Ayyash | add . (full stop)
10 | Cloud+ |  | Sameer.Ahmed | Replace "EPC Contractor" with "PURCHASER" throughout all documents
11 | Typewritten Text |  | Mohamed Ayyash | align
12 | Ellipse |  | Mohamed Ayyash
13 | Arrow |  | Mohamed Ayyash
14 | Ellipse |  | Mohamed Ayyash
15 | Typewritten Text |  | Mohamed Ayyash | align
16 | Arrow |  | Mohamed Ayyash
17 | Arrow |  | Mohamed Ayyash
18 | Ellipse |  | Mohamed Ayyash
19 | Typewritten Text |  | Mohamed Ayyash | align
20 | Callout |  | Mohamed Ayyash | align with bottom
21 | Arrow |  | Mohamed Ayyash
22 | Callout |  | Mohamed Ayyash | 60% & 90%
23 | Arrow |  | Mohamed Ayyash
24 | Cloud+ |  | Ahmed Marhoon | These activities are major milestones for the package and it is mandatory to be attended by Client representatives. Attendees list to be updated based on the agreed project matrix.
25 | Call-out |  | Ahmed Marhoon | Correct spilling to ESD instead of EDS
26 | Call-out |  | Ahmed Marhoon | Add CHAZOP
27 | Call-out |  | Ahmed Marhoon | The list shall refer to the applicable sections of the BMPS-J series (e.g. J2, J3, J6 ...etc) to cover all the requirements.
28 | Call-out |  | Ahmed Marhoon | What about SAT?
29 | Arrow |  | Ahmed Marhoon
30 | Call-out |  | Ali Abbas | All BMPS applicable Instrumentation standard and typical drawings to be given to the vendor.
31 | Line |  | Julio.Aguilar
32 | Line |  | Julio.Aguilar
33 | Line |  | Julio.Aguilar
34 | Line |  | Julio.Aguilar
35 | Text Box |  | Julio.Aguilar | Remove bullets and move these statements to be part of only one bullet point. See same statement in the section 5.9.
36 | Arrow |  | Julio.Aguilar
37 | Arrow |  | Julio.Aguilar
38 | Line |  | Julio.Aguilar
39 | Line |  | Julio.Aguilar
40 | Text Box |  | Sankara | Indicate Area Classifications as per BMPS-P2, which is based on API 505
41 | Arrow |  | Sankara
42 | Call-out |  | Ahmed Marhoon | Add a note to include the nozzles for the emission monitoring devices in suppliers scope. Access to the nozzles shall also be in suppliers scope. Final design of the system shall be finalized with the PEMS/SEMS vendor.
43 | Cloud+ |  | Ahmed Marhoon | Replace "contractor" with "client". All documents shall be generated per project specifications and agreed formats (e.g. SPI). Typical
44 | Call-out |  | Ahmed Marhoon | Add a note to the supplier to design system based on the approved PID and BMPS (meeting the final area classification)
45 | Call-out |  | Ahmed Marhoon | - Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement for the FD fans specified for the HP Boilers. - Instruct the supplier to sourc
46 | Callout |  | Julio.Aguilar | Remove information inside this brake
47 | Cloud |  | Julio.Aguilar
48 | Text Box |  | Sankara | JV to clarify how the dual drive system performs from Operation & Maintenance points of view
49 | Arrow |  | Sankara
50 | Callout |  | Mohamed Ayyash | replace ; with .
51 | Arrow |  | Mohamed Ayyash
52 | Callout |  | Sameer.Ahmed | As the Fan will be driven by steam turbine and elect motor on the same shaft, Supplier confirmation is needed that maintenance can be carried out on the electric motor while the boiler is in service with the fan being driven by the steam turbine and vice versa. Also, the type of clutch engagement during high speed rotation to be specified.
53 | Callout |  | Julio.Aguilar | Replace "manufacturer" by "Supplier" throughout all document
54 | Callout |  | Mohamed Ayyash | delete ;
55 | Arrow |  | Mohamed Ayyash
56 | Arrow |  | Mohamed Ayyash
57 | Call-out |  | Ahmed Marhoon | Vendor's commissioning assistance for the BMS during SAT is required.
58 | Arrow |  | Mohamed Ayyash
59 | Typewritten Text |  | Mohamed Ayyash | move
60 | Call-out |  | Ahmed Marhoon | Add a note on requirement to comply with BMPS-J9.
61 | Cloud+ |  | Ahmed Marhoon | Either PDG or PDIT. Type of differential pressure measurement/monitoring shall be based on the final approved PID and in accordance with BMPS-A3.
62 | Cloud+ |  | Sameer.Ahmed | Replace "Contractor" with "PURCHASER" throughout all documents
63 | Ellipse |  | Mohamed Ayyash
64 | Arrow |  | Mohamed Ayyash
65 | Typewritten Text |  | Mohamed Ayyash | move forward, align with top
66 | Call-out |  | Ahmed Marhoon | Add: and process data.
67 | Call-out |  | Ahmed Marhoon | Refer the supplier to BMPS-J18 and update this section accordingly.
68 | Cloud+ |  | Ahmed Marhoon | TMR "Woodward 5009 FT (or latest) is required per project specifications.
69 | Cloud+ |  | Sameer.Ahmed | Remove "more stringent than government emission limit"
70 | Ellipse |  | Mohamed Ayyash
71 | Callout |  | Mohamed Ayyash | align with top
72 | Callout |  | Mohamed Ayyash | space
73 | Callout |  | Mohamed Ayyash | space
74 | Callout |  | Sameer.Ahmed | add "to"
75 | Callout |  | Sameer.Ahmed | add "/"
76 | Callout |  | Mohamed Ayyash | , start up
77 | Callout |  | Sameer.Ahmed | How about training of the Owner's personnels?