## 000-G-GRD-60001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Isamu | Please list all tag numbers of the pumps and drivers in question and service description. unit number, etc.
2 | Callout | 3 | Isamu | There are no priority documents and this issue has been discussed with upper management. Please meet or talk with Mr. Isamu Kuniyama to solve this issue (to delete or reward according to previous conclusions)
3 | Text Box | 4 | Omran A | For the safe operation, the WWG system cabinet shall have a Local HMI screen (monitoring and controlling with different security level/privilege). Local HMI shall have the same functionality of remote HMI/SCADA). This shall be reflected on ROC, MOC and SOC
4 | Callout | 4 | alexis.martinez | Include the document title for 076551C-000R-SR-0910-004
5 | Text Box | 4 | Hasan Asad | As per BMPS-G9, the seal Supplier shall consider High Consequence Pump for seal selection.
6 | Callout | 5 | Isamu | add ( change over mechanism, fill/ vent and drain)
7 | Text Box | 5 | Isamu | This oil pump is expected to be 5 ~ 10 kw in power. Any steam turbine of this size comply with API 611 !!!!? Please consider giving space to manufacturer standard
8 | Callout | 5 | rob.urban | but steam turbine drive is required
9 | Callout | 6 | Isamu | Please note that shaft driven oil pump is not reliable if ever can be provided and vaialable and further more, no chance to meet with API 676. Please revise for all oil pumps to be motor driven and meet with Isamu Kuniyama (Mr) to discuss).
10 | Text Box | 7 | Hasan Asad | As per BMPS-A1, for large pump (1000 HP or greater), 3 axial displacement probes shall be provided.
11 | Text Box | 8 | Omran A | Prior to FAT, all documents & drawings such as FAT/IFAT procedure, Modbus registers, system architecture, drawings, etc... shall be submitted to BAPCO for review and comments. This shall be reflected on ROC, MOC and SOC
12 | Callout | 8 | alexis.martinez | Include the document title for 000-A-PRI-50012-001
13 | Text Box | 9 | Omran A | system architecture to be prepared as well. This shall be reflected on ROC, MOC and SOC
14 | Text Box | 9 | Omran A | CHAZOP to be included
15 | Text Box | 9 | Omran A | Prior to placing any software or hardware order, contractor shall obtain Bapco's approval first.
16 | Text Box | 9 | Omran A | BAPCO team Automation & instrumentation representative. This shall be reflected on ROC, MOC and SOC
17 | Text Box | 9 | Omran A | & IFAT
18 | Text Box | 9 | Omran A | This shall be reflected on ROC, MOC and SOC
19 | Callout | 11 | alexis.martinez | Include the document title for 076551C-000R-MR-0910-004
20 | Callout | 13 | Isamu | replace with " NPSHR test shall be carried out at the same number of points as that of flow rate points. NPSHR curve shall be plotted on the Q-H curve along with Efficiency and horse power and shall be submitted with quotation and all other rounds of vendor print requirements
21 | Text Box | 14 | Omran A | Local Indication shall be Panel mounted HMI with graphical representation. This shall be reflected on ROC, MOC and SOC
22 | Text Box | 14 | Omran A | Remote indication shall be Train-View SCADA that supports OPC UA, OPC DA and OPC HDA. This shall be reflected on ROC, MOC and SOC
23 | Text Box | 14 | Omran A | Graphical/animated representations for startup sequence shall be incorporated in remote & local HMIs for the entire systems. This shall be reflected on ROC, MOC and SOC
24 | Text Box | 14 | Omran A | All systems (HMIs & their Control Systems) and subsystems shall have the capabilities to be integrated to GPS Clock for the purpose of time synchronization. Time synchronizations shall not adversely affect the systems/plant operation. This shall be reflected on ROC, MOC and SOC
25 | Text Box | 14 | Omran A | supplied systems shall comply with IEEE/ IEEE Std C37.1 Standards, and Analysis of Systems Used for Supervisory Control, Data Acquisition, and Automatic Control. This shall be reflected on ROC, MOC and SOC
26 | Text Box | 14 | Omran A | Supplied Control systems shall have redundancy in CPU, communication modules and power supply units. This shall be reflected on ROC, MOC and SOC
27 | Callout | 14 | Jong.Ahn | pls add "up to I/O cards."
28 | Call-out | 14 | Ali Abbas | The instrumentation scope and design shall take into consideration all applicable BMPS-Js and BMPS-A3 (in addition to quoted BMPS-J6 specification), typical/standard drawings and AVL in addition to all deliverables listed under CDRL. Any deviation from any BMPSs to be listed reviewed/approved by owner.
29 | Text Box | 15 | Omran A | To ensure that all systems are designed as per Bapco's specifications, Bapco's instrumentations & systems representatives shall be involved on all Kick-off meetings, FAT, IFAT, etc.. This shall be reflected on ROC, MOC and SOC
30 | Text Box | 16 | Omran A | and Systems architectures for all systems/subsystems
31 | Text Box | 16 | Omran A | This shall be reflected on ROC, MOC and SOC
32 | Text Box | 18 | Omran A | Control Systems spare parts shall be included.E32
33 | Text Box | 18 | Omran A | , Instrumentations and Control Systems.
34 | Text Box | 18 | Omran A | ,Control Systems
35 | Text Box | 18 | Omran A | This shall be reflected on ROC, MOC and SOC
36 | Text Box | 18 | Omran A | This shall be reflected on ROC, MOC and SOC
37 | Callout | 18 | Jong.Ahn | pls "and Instrumentations"
38 | Call-out | 18 | Rashed Almudahka | ADD "and with compliance to attachment-1 found in volume-2, section-6, sub-section-6.5 of FEED package
39 | Text Box | 19 | Omran A | Laptop shall be loaded with perpetual software.
40 | Text Box | 19 | Omran A | Laptops shall be loaded with latest Anti-Virus & all necessary Software for the maintenance of the equipment
41 | Text Box | 19 | Omran A | This shall be reflected on ROC, MOC and SOC
42 | Text Box | 19 | Hasan Asad | 1. The Vendor/Supllier shall provide LCCA report for 20 years including the main equipment and associated systems. 2.Mechanical seal selection shall be in accordance to Seal OEM selection chart and High Consequence Pump criteria as specified in BMPS G9 shall be considered as well. 3.Bearing life shall be calculated and provided. 4.Owner standardized on John Crane mechanical seal with a long term contract for reliability services, seal repair and test and supply of inventory. Owner preference is John Crane due to standardization and seal spare interchangeability. 6.The seal API plan shall be accessible and a filling cart is provided for filling the seal pot.