## 000-S-GRD-80010-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Stamp | 1 | Nalini Mohan
2 | Text Box | 1 | Mahdi Ali | Add document title in the header
3 | Text Box | 1 | Nalini Mohan | Owner has reviewed and commented on the MR package submitted on Contractor’s request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3
4 | Callout | 1 | balagangadhar.k | Match Date Format, typ. for all documents
5 | Callout | 1 | Julio.Aguilar | Package number to be included
6 | Text Box | 2 | Jeung.Kim | Is this a separate deliverables? Please note that this review code is applicable for MR and MDS.- typical comment
7 | Arrow | 2 | Jeung.Kim
8 | Callout | 4 | Nalini Mohan | As defined in earlier MRs for SOC Documents Priority should be changed.
9 | Text Box | 5 | Mahdi Ali | What is Part 2? Is it sheet 2??
10 | Callout | 5 | Salman Jaffer | EPC Contractor shall include training of OWNER staff (both at job site and subcontractor shop) in line with the requirements of Exhibit F of Annex 12 as part of the Vendor scope of supply.
11 | Callout | 5 | Sameer.Ahmed | Be consistent, use "II" or "2"
| Highlight | 5 | Mahdi Ali
| Arrow | 5 | Mahdi Ali
| Highlight | 5 | Mahdi Ali
12 | Text Box | 6 | Hasan Asad | Change as per new equipment list
13 | Call-out | 6 | Ali Abbas | and IFAT
14 | Cloud | 6 | Hasan Asad
15 | Call-out | 6 | Ali Abbas | Owner representative to be added.
16 | Callout | 6 | Robert.Kawitzki | is
17 | Callout | 6 | Syed Ahmed | Rodding points to be provided.
18 | Call-out | 6 | Hasan Al Noaimi | DCS SAT
19 | Text Box | 6 | Hasan Asad | and filteration system
20 | Call-out | 6 | Ali Abbas | CHAZOP if applicable
21 | Call-out | 6 | Ali Abbas | Need to add control narrative
22 | Rectangle | 6 | Nalini Mohan
23 | Call-out | 7 | Hasan Al Noaimi | Accessibile rodding points
24 | Call-out | 7 | Hasan Al Noaimi | Steam jacketting not tracing
| Line | 7 | Mahdi Ali
25 | Callout | 7 | Salman Jaffer | add bullet
26 | Text Box | 7 | Mahdi Ali | Change as per new equipment numbers
| Strikethrough | 8 | Mahdi Ali
27 | Callout | 8 | Salman Jaffer | 094FA9402A/B but it should follow the new numbing
28 | Text Box | 8 | Mahdi Ali | Use correct equipment number
29 | Text Box | 8 | Hasan Asad | Add: Cleaning facility/ports
30 | Callout | 8 | Salman Jaffer | Provision of Sunshade/shelter shall be confirmed after selection of proposed chemicals and their MSDS requirements
31 | Callout | 9 | BD Mori | Cooling Tower water treatment chemical dosing facility viz. the chemical storage tank/s, stand for the storage tank/s, dosing pumps
| Strikethrough | 9 | Mahdi Ali
| Strikethrough | 9 | Mahdi Ali
| Strikethrough | 9 | Mahdi Ali
32 | Callout | 9 | Salman Jaffer | Please refer to BMPS-E8
| Text Box | 9 | BD Mori
| Strikethrough | 9 | Mahdi Ali
| Strikethrough | 9 | Mahdi Ali
| Strikethrough | 9 | Mahdi Ali
| Strikethrough | 9 | Mahdi Ali
33 | Callout | 10 | Robert.Kawitzki | jacketed
34 | Callout | 10 | Salman Jaffer | Vendor shall provide Dust suppression facility as required.
| Strikethrough | 10 | Mahdi Ali
| Strikethrough | 10 | Mahdi Ali
35 | Callout | 11 | Salman Jaffer | Special tools requirement to be provided as required.
| Strikethrough | 11 | Mahdi Ali
36 | Callout | 11 | balagangadhar.k | 094FA9401
37 | Text Box | 11 | Nalini Mohan | Contractor ensure the scope of supply for the field instruments of F&G system which are not included in the P&ID
| Strikethrough | 11 | Mahdi Ali
| Arrow | 12 | Nalini Mohan
38 | Callout | 12 | Nalini Mohan | through prequalification exercise
39 | Callout | 12 | BD Mori | Duty Specification (094-S-DAT-00001-001) and
40 | Text Box | 14 | Hasan Asad | Access for replacing the belt shall be considered and provided.
41 | Text Box | 15 | Hasan Asad | Cover with anti-static rubber to avoid sparks.
42 | Text Box | 15 | Hasan Asad | Experience proved that poly nozzles get blocked due to CS piping rust. Consider alternative material.
| Arrow | 15 | Hasan Asad
43 | Callout | 15 | Nalini Mohan | Include alternate material suggestion as optional price,
44 | Callout | 18 | Nalini Mohan | As clarified in query T1759 deluge system shall be provided for sulphur conveyor belts
45 | Callout | 21 | Robert.Kawitzki | 750mm
46 | Callout | 21 | Syed Ahmed | With rodding out facility as per BMPS-L7.
47 | Callout | 21 | Robert.Kawitzki | 1000mm
| Line | 21 | Robert.Kawitzki
48 | Callout | 21 | Julio.Aguilar | BMPS-G3 to be included
| Line | 21 | Robert.Kawitzki
49 | Callout | 22 | Syed Ahmed | Review the requirement of chemical cleaning or steam cleaning of the filter and provide necessary facility.
50 | Text Box | 23 | Ebrahim | Shall be TEFC, as per clause 5.4 of BMPS-P19
| Ellipse | 23 | Ebrahim
51 | Call-out | 24 | Ali Abbas | dual
52 | Call-out | 24 | Ali Abbas | common faults and diagnostic systems alarms to be included.
53 | Call-out | 24 | Ali Abbas | Add all others applicable BMPSs, CDRL, Standard, Typical J drawings and AVL
54 | Callout | 24 | Salman Jaffer | 094-S-DAT-00001-001
55 | Call-out | 25 | Ali Abbas | Owner preference if the control and logic is implemented in the DCS. Need to discuss with package vendor the technical details.
56 | Callout | 25 | Syed Ahmed | Thermo fluid air cooler on / off
57 | Callout | 25 | Syed Ahmed | Thermo fluid circulation pump on / off
58 | Callout | 26 | Nalini Mohan | Basis for allowable nozzle loads to be clarified
59 | Call-out | 27 | Ali Abbas | Deviation list to include deviation from BMPSs specifications and standard drawings.
60 | Callout | 29 | Nalini Mohan | Supplier shall specifically advise the requirement for Nitrogen
61 | Callout | 29 | BD Mori | Chemicals consumption summary
62 | Callout | 29 | BD Mori | Effluent summary
63 | Text Box | 31 | Hasan Asad | The Maintenance Consideration report shall include the cleaning and inspection requirement for the solidification system and the collecting conveyor as to aviod the accumulation of sulphur dust in the system. The solidification system shall have a daily checklist to ensure sulphur solidification quality is maintained.
64 | Text Box | 31 | Hasan Asad | 1. Steel belt for the Granulation unit shall be considered as this is long lead item. 2. Spare gearbox and motor for the collecting conveyor.