## 019-K-DAT-00003-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Isamu | Delete
2 | Callout | 1 | Mohamed Ayyash | Delete c
3 | Callout | 1 | Mohamed Ayyash | No. (Typo) apply to all sheets
4 | Text Box | 1 | Ahmed Marhoon | 7. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 8. All the BN machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 9. Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 10. Assistance and involvement of the vendor during CHAZOP/Hazop workshops/studies to be considered. 11. Explanatory notes to be added on the requirement of having the control performed in the plant DCS and safety functions in ESD system. 12. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 13. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting …etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 14.Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval.
5 | Line | 1 | Isamu
6 | Callout | 1 | Mohamed Ayyash | 2HCU (apply on all sheets)
7 | Cloud | 1 | Mohamed Ayyash
8 | Text Box | 1 | Ahmed Marhoon | The following are comments related to instrumentation and control: 1. All applicable BMPS-J series to be referenced (such as J2, J3, J6, J31 …etc) for the supplier to comply with. For anti-surge system, BMPS-J16 and for turbine Speed Governor, BMPS-J18 to be referenced for compliance. 2. TTSJV is requested to ensure that all the specific technical/functional requirements (including AVL) are covered and detailed in the requisition specification that will be sent out to suppliers. In case this document would be the only one for MR, then all the relevant BMPS to be included in the Data Sheet notes. 3. Vendors to be notified on the fact that the final design of the system shall include all the Hazop3/SIL recommendations and approved PID post-EPC-development. 4. Since the Data Sheet is issued separately, the consistency between the different documents, that may be part of the requisition, could not be verified and hence it is the contractor’s responsibility to update the other documents impacted by any of the comments on this Data Sheet and vice versa. 5. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. 6. Requirement of MCM to be detailed with the supplier. Reference to BMPS-J15 MCM to be added accordingly.
9 | Call-out | 2 | Sameer Foujdar | Rated pressure and temperature values are not as per BMPS A1 to be verified and corrected.
10 | Call-out | 7 | Sameer Foujdar | Turning gear is it required for turbine to be verified and confirmed.
11 | Call-out | 9 | Sameer Foujdar | Speed indication required in the field panel from governor.
12 | Text Box | 10 | Hasan Asad | Shall include Mechanical and Electronic Trip
13 | Text Box | 11 | Hasan Asad | The vendor shall provide complete LCCA report considering the different parts of the turbine.
14 | Cloud+ | 11 | A.Jabbar Mahmood | The minimum operating CW supply pressure is 65 psig at unit B.L as per BMPS A3. Check and verify
15 | Callout | 11 | Mohamed Ayyash | Align
16 | Cloud+ | 11 | A.Jabbar Mahmood | The minimum operating CW return pressure is 36 psig as per BMPS A3. Check and verify