## 043-E-DAT-00001-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC | Will be incorporated into PO Material Requisition, after revising the equipment numbering officially. | N
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs | All have been implemented, but will be updated at PO requisition as per the Homogenization Procedure (000-A-PRO-50006-1) revision. | Y
3 | Cloud+ | Page 2 | Sameer.Ahmed | As per BMPS-A1 8.2.3, O.D. 25.4 (1) | Tube OD can be used from 1 inch to 1.5 inch, as per BMPS-E7 para. F.2.4.2, and will be defined during TBE. | N
4 | Callout | Page 2 | BD Mori | Specify the estimated highest temperature at transient operating conditions or upset scenario e.g start-up, shutdown, electrical power failure or any other operating scenario leading to the highest possible temperature expected at inlet to the each air cooler. Based on the highest temperature if required the vendor shall perform FEA analysis. | No upset case required for higher temperature than design condition. To be reviewed with FEED/Licensor, if required. | N
5 | Text Box | Page 3 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC | Will be incorporated into PO Material Requisition, after revising the equipment numbering officially. | N
6 | Callout | Page 3 | Salman Jaffer | a) Please refer to Bid Query T1383 for the requirement for automatic louver b) Type 'B' manifold. c) The degree of the slop for free draining purpose per PIDs | a) Automatic louver has been applied at datasheet for air coolers of Sulphur Block as per T1383. b) Will be clarified at TBE stage c) Will be clarified at TBE stage | N