## 044-E-DAT-00002-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
2 | Callout | Page 1 | Salman Jaffer | Unit name
3 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
4 | Callout | Page 2 | Saeed Taher | SA 240 TP 316L
5 | Cloud+ | Page 2 | Sameer.Ahmed | This length is not as per BMPS-A1 8.2.3
6 | Callout | Page 2 | BD Mori | Specify the estimated highest temperature at transient operating conditions or upset scenario e.g start-up, shutdown, electrical power failure or any other operating scenario leading to the highest possible temperature expected at inlet to the each air cooler. Based on the highest temperature if required the vendor shall perform FEA analysis.
7 | Callout | Page 2 | BD Mori | PFD value is 22.11. Check and verify
8 | Callout | Page 2 | BD Mori | Corrosion allowance is deleted. FEED value is 6 mm
9 | Text Box | Page 3 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
10 | Callout | Page 3 | Salman Jaffer | a) Please refer to Bid Query T1383 for the requirement for automatic louver b) Type 'B' manifold. c) The degree of the slop for free draining purpose per PIDs
11 | Callout | Page 3 | Syed Ahmed | Note 1 to be added: This data sheet is applicable also to identical equipment 045E4511 no.4 TGTU (in addition please change the cooler number after SOC modifying)
12 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3