## 048-E-DAT-00002-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC | Will be incorporated into PO Material Requisition, after revising the equipment numbering officially. | N
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs | All have been implemented, but will be updated at PO requisition as per the Homogenization Procedure (000-A-PRO-50006-1) revision. | Y
3 | Cloud+ | Page 2 | Jawad Alawi | Refer to T1568 for tubes material | Comment incorporated. The material changed to SA179. | Y
4 | Cloud+ | Page 2 | Sameer.Ahmed | This length is not as per BMPS-A1 8.2.3 | As per BMPS-A1 and BMPS-E7, preferred tube length is 16, 30, 42 ft. However, this limitation can be discussed during the EPC stage, as per Bid Clarification T883 for the economical reasons. It can be deeply discussed after TBE. | N
5 | Callout | Page 2 | BD Mori | Specify the estimated highest temperature at transient operating conditions or upset scenario e.g start-up, shutdown, electrical power failure or any other operating scenario leading to the highest possible temperature expected at inlet to the air cooler. Based on the highest temperature if required the vendor shall perform FEA analysis. | No upset case required for higher temperature than design condition. To be reviewed with FEED/Licensor, if required. | N
6 | Text Box | Page 3 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC | Will be incorporated into PO Material Requisition, after revising the equipment numbering officially. | N
7 | Callout | Page 3 | Salman Jaffer | a) Please refer to Bid Query T1383 for the requirement for automatic louver b) Type 'B' manifold. c) The degree of the slop for free draining purpose per PIDs | a) Automatic louver has been applied at datasheet for air coolers of Sulphur Block as per T1383. b) Will be clarified at TBE stage c) Will be clarified at TBE stage | N
8 | Callout | Page 3 | BD Mori | Do not use acronyms: Low Severity Wet H2S Service (LSS) | Comment incorporated. | Y