## 048-E-DAT-00003-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC | Will be incorporated into PO Material Requisition, after revising the equipment numbering officially. | N
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs | All have been implemented, but will be updated at PO requisition as per the Homogenization Procedure (000-A-PRO-50006-1) revision. | Y
3 | Callout | Page 1 | BD Mori | LP | Retained. Service name is changed to 'ARU Steam Condenser.' | N
4 | Cloud+ | Page 2 | Sameer.Ahmed | As per BMPS-A1 8.2.3, O.D. 25.4 (1) | Tube OD can be used from 1 inch to 1.5 inch, as per BMPS-E7 para. F.2.4.2, and will be defined during TBE. | N
5 | Cloud+ | Page 2 | Sameer.Ahmed | Add note: Length to be as per BMPS-A1 8.2.3 | As per BMPS-A1 and BMPS-E7, preferred tube length is 16, 30, 42 ft. However, this limitation can be discussed during the EPC stage, as per Bid Clarification T883 for the economical reasons. It can be deeply discussed after TBE. | N
6 | Callout | Page 2 | balagangadhar.k | Steam inlet to the air cooler is from a vessel operating at atmospheric pressure. Inlet Steam temperature shall be saturation temperature at vessel operating pressure which is 212 F. Please change the duty, inlet temperature, properties and flow rate. Flow rate should be higher than this due to flashing of additional condensate into steam. | Refer to H&MB stream number #323. 222 F is for V4813 and E4813. But, exact condition to be checked. | N
7 | Callout | Page 3 | Salman Jaffer | Type 'B' manifold. | Will be clarified with vendor during TBE. | N
8 | Callout | Page 3 | Syed Ahmed | LP | Retained. Service name is changed to 'ARU Steam Condenser.' | N
9 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3 | Minimum design temperature has been called many BMP specifications, especially BMPS-E7. No need to specify BMP-A3. | N