## 341-A-BOD-00001-001-RA-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | BD Mori | The Instrument Air and Yard Air consumption may change during the detailed design. Therefore, TTSJ shall resubmit the revised BOD for approval after the consumption values are finalized.
2 | Text Box | 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
3 | Callout | 3 | Sameer.Ahmed | Add: "and air make-up for the existing refinery units
4 | Call-out | 3 | Edgardo | This paragraph refers to the scoping report done during Pre-FEED and may no longer be valid for the EPC phase. It is suggested to delete this paragraph.
5 | Cloud+ | 3 | Sameer.Ahmed | Remove "foreseen"
6 | Cloud+ | 3 | Sameer.Ahmed | existing Gas Turbines (GT)
7 | Text Box | 3 | Mahdi Ali | Equipment numbers shall be as per BMPS-A8
8 | Text Box | 4 | Hasan Asad | Total no. of oil mist system shall be reconfirmed by JV.
9 | Call-out | 4 | Ali Abbas | Most of these air consumption estimates for a, b & c above are based on FEED and needs to be validated based on detailed engineering data.
10 | Call-out | 4 | Ebrahim | For HV motors in Zone 2 and Zone 22, the motor enclosure shall be Ex-d or Ex-e. Refer to Clarification Request T-107
11 | Text Box | 5 | Jeung.Kim | All these consumptions have to be verified and finalized in the course of detail design development by the Contractor- typical comment
12 | Cloud+ | 5 | Julio.Aguilar | Note 25 doesn't exist. Note to be 14. Please confirm
13 | Callout | 5 | Salman Jaffer | Change unit name to 1HRU
14 | Cloud+ | 5 | Sameer.Ahmed | These documents' numbers are referenced to FEED documents. TTSJV to update as per the new documents numbering
15 | Callout | 5 | Sameer.Ahmed | Add: and hence the consumption is not counted as part of the total Process Inst. Air requirement
16 | Callout | 5 | Salman Jaffer | Please refer to Bid Query T1545
17 | Cloud+ | 5 | Sameer.Ahmed | Remove suffix
18 | Cloud+ | 6 | Sameer.Ahmed | Remove suffix
19 | Cloud+ | 6 | Sameer.Ahmed | Align the table header
20 | Cloud+ | 6 | Sameer.Ahmed | These documents' numbers are referenced to FEED documents. TTSJV to update as per the new documents numbering
21 | Callout | 6 | Salman Jaffer | Change to Refinery South Flare
22 | Callout | 7 | Julio.Aguilar | Review the number of motors listed in this table and revise their air consumption base on the supplier data
23 | Callout | 7 | Julio.Aguilar | Add a note 2: Mention the tag number for the biggest motor.
24 | Text Box | 8 | Sameer.Ahmed | Refer Table 1.2
25 | Text Box | 8 | Sameer.Ahmed | Refer Table 1.1
26 | Text Box | 8 | Sameer.Ahmed | Refer Table 1.1
27 | Text Box | 8 | Sameer.Ahmed | Refer to 1.1.c.
28 | Callout | 11 | Sameer.Ahmed | Note.1
29 | Call-out | 11 | Ali Abbas | Which process units? need to specify at each end.
30 | Callout | 11 | Sameer.Ahmed | Note.1
31 | Callout | 11 | BD Mori | Include Flow
32 | Text Box | 11 | Sameer.Ahmed | Note-1: Conditions refer at furthest user inside the Process Unit.
33 | Cloud+ | 13 | Sameer.Ahmed | Explain how the compressor can operate at zero capacity
34 | Call-out | 14 | Ali Abbas | The estimate of 0.75 scfm is based on max. air flow rate to each valve/user. However, during plant in steady state, the consumption is well below this figure of 0.75 scfm per user. This may lead to venting a lot of air when two compressors are running! Is this a valid scenario and is it acceptable?
35 | Call-out | 15 | Ali Abbas | in the block diagram, states 95 in certain block of process unit. Refer to page 11, figure 3.1 comments.
36 | Callout | 15 | Sameer.Ahmed | Remove suffix "u"
37 | Callout | 15 | Sameer.Ahmed | Remove suffix "u"