## 341-S-DAT-00001-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 4 | Ali Abbas | ensure reference to BMPS-J series specifications, typical and standard drawings and AVL are included.
2 | Callout | 2 | BD Mori | As per Basis of Design document it is 31 degF. Recheck.
3 | Text Box | 1 | Dowon Pyun | This data sheet is not approved because the preceding document of MSD has not submitted and no revision management from FEED data sheet have completed according to agreed procedures. Therefore, Contractor is advised that the Company's comments to be sent this time have not been completed accordingly.
4 | Callout | 2 | Dowon Pyun | 127 psig at compressed air receiver as an inlet condition. Contractor to recheck battery limit conditions
5 | Callout | 3 | Dowon Pyun | Contractor to confirm max moisture content as one of performance guarantee at package outlet
6 | Callout | 3 | Dowon Pyun | Contractor Supplier to confirm max. permitted bypass time without any repercussions on regeneration loop performance
7 | Callout | 4 | Dowon Pyun | Add "Air dryers are heatless type"
8 | Callout | 4 | Dowon Pyun | Add "Supplier shall propose max. pressure drop before cleaning"
9 | Call-out | 2 | Edgardo | For clarity, please insert the word "Note" before the note number, ie, it should read "Note 1". This comment applies to all note numbers.
10 | Callout | 2 | Isamu | Room for information on "Filter Effciency" " ISO Quality Class"..etc
11 | Callout | 2 | Isamu | Heatlesqs Desiccant ??
12 | Callout | 2 | Isamu | Provide line(s) to indicate Applicable standard such as ISO 8573.1
13 | Callout | 2 | Isamu | Provide line(s) to indicate air quality such as "salt laden" "Saliferous".
14 | Callout | 3 | Isamu | Dried air
15 | Text Box | 1 | Jeung.Kim | General comment: Contractor has to verify the design capacity through the development of the utility consumption summary
16 | Text Box | 4 | Jong.Ahn | SOC to clarify the control scheme of this package.
17 | Text Box | 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
18 | Cloud+ | 4 | Julio.Aguilar | Capacity to be revised in case this figure change.
19 | Cloud+ | 4 | Julio.Aguilar | spelling error
20 | Cloud+ | 4 | Julio.Aguilar | spelling error
21 | Call-out | 1 | Mahdi Ali | Remove the word 'letter'
22 | Text Box | 1 | MAK | Use the latest cover page which is part of the Homogenization Procedure. SOC shall coordinate with JV Directorate.
23 | Callout | 3 | Saeed Taher | BMPS-B5
24 | Callout | 4 | Saeed Taher | To be reviewed and approved during EPC