## 000-J-BLD-60002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Omran A | HMI/
2 | Callout | 1 | Danut.Dragan | "FF TRUNK"
3 | Callout | 1 | Danut.Dragan | "NOR" shall read "NON-" "NON-FF" or "NON-IS", etc, in notes and drawing, (FF, IS and any other)
4 | Callout | 1 | Danut.Dragan | "Segment" shall read "Spur"
5 | Callout | 1 | Danut.Dragan | "SEGMENT" shall read: "INTERMEDIATE JB" or "SEGMENT PASS THROUGH JB". I think "INTERMEDIATE" reflects better the fact and it is more suggestive.
6 | Text Box | 1 | Abdul Majeed | / IEPCS
7 | Text Box | 1 | Abdul Majeed | 4. DCS PRM (Plant Resources Manager)
8 | Callout | 1 | Danut.Dragan | Abbreviations should be completed at least with: "I/E", "UPS", "VAC", "MCC", "UPS", "HVAC", "V-NET/IP"
9 | Text Box | 1 | Ahmed Habib | acknowledge
10 | Callout | 1 | Danut.Dragan | Battery Limit - Line-type or other might be used for FIELD / CR / Substation / etc, separation.
11 | Text Box | 1 | Omran A | CAT6 (copper)
12 | Callout | 1 | Danut.Dragan | complete with "BLOC DIAGRAM ..."
13 | Callout | 1 | Danut.Dragan | Cross wiring is the main function of the Marshalling Cabinet, so there is no need to mention
14 | Text Box | 1 | Omran A | Dual Link
15 | Text Box | 1 | Omran A | Dual Link
16 | Text Box | 1 | Omran A | Dual Serial Link
17 | Text Box | 1 | Omran A | Dual Serial Link
18 | Callout | 1 | Danut.Dragan | Equipment like: -Portable EWS -DCS / ESD / EWS -any other Operation Station -printers, Also, all the symbols used in the drawing shall be depicted and described in a Legend. The Legend shall be unique for all relevant Drawings in the project.
19 | Text Box | 1 | Ahmed Habib | General comment: Integration of FAS & GAS to be discussed and finalized at detail design
20 | Text Box | 1 | Omran A | General Comment: 1- For DCS: a) One EWS shall be included at each SRR. b) Vendor to recommend EWS requirement in RSCB. 2) Redundant DCS OPC to be included. Location to be discussed during detail design. 3- Connection between process systems within the same SRR/Control Room shall be CAT6 (Copper) and not FO.
21 | Callout | 1 | Danut.Dragan | MUX from Multiplexer vs MUX from Marshalling ESD Cabinet. It is confusing. Multi-Input might be used instead for Multiplexer.
22 | Text Box | 1 | Bachir M | New Communications Cabinet to be shown for all network connections between systems in SRR and RSCB.
23 | Text Box | 1 | Ahmed Habib | Plant
24 | Callout | 1 | Danut.Dragan | please include: "... NON-CRITICAL ..."
25 | Callout | 1 | Danut.Dragan | please include: "... TRANSMITTER ..."
26 | Text Box | 1 | Ahmed Habib | Point
27 | Text Box | 1 | Abdul Majeed | PRM PLANT RESOURCES MANAGER IEPCS INTEGRATED ELECTRICAL PROTECTION CONTROL SYSTEM
28 | Text Box | 1 | Omran A | Refer to general comment
29 | Text Box | 1 | Abdul Majeed | Segregation 3 systems, a cabinet for per system to have seperate cabinet tag number.
30 | Callout | 1 | Danut.Dragan | shall read "MEASUREMENTS"
31 | Callout | 1 | Danut.Dragan | The JB and Spurs shall be represented correct as TREE Topology according with BMP-J-059695.
32 |  | 1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
33 | Callout | 1 | Danut.Dragan | There is no need to mention in any cabinet: "REDUNDANT CTRL." "CROSS WIRING" "IS ISOLATOR" It is mentioned in Specs and by default understood. Control System Cabinets would be better represented in a double box to show redundancy, also for Servers and other System Dual Redundant devices / Cabinets:
34 | Text Box | 1 | Omran A | this is
35 | Text Box | 1 | Ahmed Habib | Typical: All (Not IS) shall be written as (Non IS)