## 000-J-BLD-60004-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Ahmed Habib | 3 Sulphur Plant
2 | Callout | 1 | Mahdi Ali | EX: 62756 P.N.: EN0815
3 | Text Box | 1 | Ahmed Habib | All FO shall be dual
4 | Text Box | 1 | Ahmed Habib | Low Lift Pump House shall be shown
5 | Text Box | 1 | Omran A | System architecture to be finalised during detail design and post site survey
6 | Text Box | 1 | Abdul Rahim | Pls add DCS monitor at Wharf Lab for entering Sample results. In two locations T-Head and Island Wharf Labs.
7 | Call-out | 1 | Ahmed Habib | Existing setup of Marshlling cabinet and I/Os shall be checked/verfied with respect to the integration of the systems to new UCB.
8 | Text Box | 1 | MAK | General Comments: 1. Use the correct border size. 2. Drawing borders files are AutoCAD blocks that contain attributed input fields that require to be completed by the Contractor. 3. Drawing borders files shall be inserted into drawings and scaled to the appropriate size. 4. In no circumstance drawings borders blocks shall be exploded or modified.
9 | Text Box | 1 | Ahmed Habib | Differentiate between both
10 | Text Box | 1 | Ahmed Habib | UCB
11 | Callout | 1 | Danut.Dragan | - Abbreviations to be incorporated: PCS, NPCB, SPCB, LSDP, SHF, SRR, UCB, HLPH, CCTV, EWS, SOE, UPS, VAC, VDU, PC, and others. - Legend: -"Legend", "Abbreviations" and "General Notes", shall be shown once in the first sheet. The document has three shee
12 | Cloud+ | 1 | MAK | NTS
13 | Text Box | 1 | Mahdi Ali | UNIT ABBREVIATINS SHALL NOT CONTAIN SPACE
14 | Callout | 1 | Mahdi Ali | REPLACE TITLE WITH MORE MEANINGFUL ONE
15 | Callout | 1 | Mahdi Ali | 0
16 | Callout | 1 | Mahdi Ali | INCORRECT UNIT DESCRIPTION
17 | Text Box | 1 | Mahdi Ali | USE LATEST BORDER THAT IS PART OF THE HOMOGENIZATION PROCEDURE
18 | Cloud+ | 1 | MAK | This is not A0 border, it's A1 border
19 | Text Box | 1 | Ahmed Habib | HLPH
20 | Text Box | 1 | Omran A | Plant Information
21 | Text Box | 1 | Ahmed Habib | Communication arrow (direction) shall be shown
22 | Text Box | 1 | Ahmed Habib | Exisitng
23 | Text Box | 1 | David.Jimenez | Please ratate document 90 degrees
24 | Cloud+ | 1 | MAK | 000 - COMMON