## 000-J-BLD-60004-002-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | NTS
2 | Cloud+ | 1 | MAK | 000 - COMMON
3 | Callout | 1 | Francis L | accommodate
4 | Text Box | 1 | Francis L | Clarify whether signal interconnections between the ESD systems between Sitra Tanks, Wharf and C3/C4 Storage are required. One critical facility is the General Shutdown pull buttons at Wharves 1 & 2, and Sitra Tanks which are to be connected to the ESD system. New signal interconnections are needed between Sitra Tanks, Wharf and C3/C4 Storage (to be considered). All associated existing cabling and switches shall be renewed.
5 | Text Box | 1 | Ahmed Habib | To be clarify, no new tank gauging system included in BMP
6 | Text Box | 1 | Omran A | final list of alarms to be decided during detail design
7 | Text Box | 1 | Omran A | System architecture to be finalised during detail design and post site survey
8 | Text Box | 1 | Omran A | why REF,it shall be SIT
9 | Callout | 1 | Francis L | This FO cable is to be site verified for cable existence and suitability (ie. no. of cores, redundancy, etc)
10 | Callout | 1 | Francis L | locations
11 | Text Box | 1 | Omran A | intake
12 | Call-out | 1 | Bachir M | There is no exisitng FO cable between Sitra and Refinery Tanks control Building
13 | Call-out | 1 | Bachir M | There is no existing FO connection between Ref. Tanks and Sitra Tanks control rooms.
14 | Text Box | 1 | MAK | General Comments: 1. Use the correct border size. 2. Drawing borders files are AutoCAD blocks that contain attributed input fields that require to be completed by the Contractor. 3. Drawing borders files shall be inserted into drawings and scaled to the appropriate size. 4. In no circumstance drawings borders blocks shall be exploded or modified.
15 | Text Box | 1 | Omran A | General note All control systems shall be servers and not PCs.
16 | Text Box | 1 | Omran A | and owner rep.
17 | Call-out | 1 | Bachir M | General comment: OPC servers to be shown in all block diagrams where servers are shown
18 | Text Box | 1 | Francis L | Note 4. Include that DCS vendor (Yokogawa Tokyo will be fully involved in the modification, implementation, testing and commissioning of the blending modification.
19 | Text Box | 1 | Ahmed Habib | General commnet: All system archticture shall be finalized/verified after site visit
20 | Callout | 1 | Francis L | Correct sheet numbering.
21 | Text Box | 1 | Omran A | workstation
22 | Cloud+ | 1 | MAK | This is not A0 border, it's A1 border
23 | Text Box | 1 | Omran A | Process Network and PI
24 | Text Box | 1 | Omran A | Plant Information
25 | Text Box | 1 | Francis L | Include in Note 14, specifying the scope of installing new pump stop bypass switches at the various locations where new pumps are to be installed. New enclosures may be needed for these switches.
26 | Call-out | 1 | Ahmed Habib | Tank Gauging upgrade is not part of BMP, also in Sitra Rosemount system will be installed instead of ENRAF system
27 | Text Box | 1 | Omran A | use different symbol Data Highway Net
28 | Text Box | 1 | Omran A | UPS
29 | Text Box | 1 | Omran A | Process Network & PI
30 | Text Box | 1 | Omran A | do you mean RSCB or LSDP?
31 | Text Box | 1 | Ahmed Habib | Repeated
32 | Text Box | 1 | Bachir M | It is not recommended to use the existing FO cables which are also used by ITD for the DCS network. We should use dedicated FO cables.
33 | Text Box | 1 | Omran A | and integrated to DCS.
34 | Text Box | 1 | Omran A | ?