## 000-J-BLD-60004-003-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | This is not A0 border, it's A1 border
2 | Text Box | 1 | Bachir M | General Comment: DCS Ethernet connection between EWS and HISs shall be shown
3 | Callout | 1 | Francis L | Clarify whether it will be Fire & Gas. Typical and applies to other similar systems.
4 | Callout | 1 | Francis L | Correct sheet no.
5 | Cloud+ | 1 | MAK | NTS
6 | Call-out | 1 | Ahmed Habib | FO shall be dual (redundant)
7 | Cloud+ | 1 | MAK | 000 - COMMON
8 | Text Box | 1 | Bachir M | This should be FO connection
9 | Call-out | 1 | Ahmed Habib | LSDP
10 | Text Box | 1 | MAK | General Comments: 1. Use the correct border size. 2. Drawing borders files are AutoCAD blocks that contain attributed input fields that require to be completed by the Contractor. 3. Drawing borders files shall be inserted into drawings and scaled to the appropriate size. 4. In no circumstance drawings borders blocks shall be exploded or modified.
11 | Text Box | 1 | Omran A | System architecture to be finalised during detail design and post site survey