## 000-J-MST-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | Delete
2 | Text Box | 1 | MAK | General Comment: Bapco Doc/Dwg No. shall be used for references in all documents and drawings.
3 | Call-out | 1 | Ali Abbas | Reference shall be made to BMPS-J31Instrumentation Installation & Testing and any deviation from this spec shall be addressed.
4 | Cloud+ | 1 | MAK | General Comment: If the scope of the document is "Method of Statement" then the title shall be revised. If it's "Specification", then the document code shall be changed from MST to TSP.
5 | Cloud+ | 3 | MAK | Bapco Doc. No.
6 | Call-out | 3 | Ali Abbas | No clear what is the intention
7 | Callout | 3 | Mahdi Ali | THE DOCUMENT TYPE IS 'MST' WITH IS A METHOD STATEMENT. THE TITLE OF THIS DOCUMENT IS SPECIFICATINO WHICH THE DOCUMENT TYPE SHOULD BE 'TSP' AND THE SCOPE INDICATES THAT THIS DOCUMENT IS A PROCEDURE WHICH SHOULD BE 'PRO'. RESOLVE THE INCONSISTENCY AND REFLECT THE CHANGE ACCORDINGLY INCLUDING ALL REFERENCES TO THIS DOCUMENT.
8 | Text Box | 3 | mohamed.waleed | Do we have a separate document for FIRE and GAS instruments or is it covered in this document ?
9 | Call-out | 4 | Ali Abbas | add SLD Segment Loop Diagram
10 | Call-out | 4 | Ali Abbas | Pls clarify as in this project we have specific names for Control Buildings and SRR?
11 | Call-out | 4 | Ali Abbas | HMI
12 | Call-out | 5 | Ali Abbas | checked
13 | Call-out | 5 | Ali Abbas | dust free
14 | Call-out | 6 | Ali Abbas | Need also a proper facility for conducting these functions such as a temporary workshop.
15 | Call-out | 6 | Ali Abbas | state title?
16 | Call-out | 6 | Ali Abbas | Need special instruction for special materials handling and government certification/clearance or special authority approval such as Nuclear level instruments
17 | Call-out | 7 | Ali Abbas | What about other systems and sub-systems such as MCM, F&G, etc.
18 | Call-out | 9 | Ali Abbas | In all above activities Owner shall have the right to witness and approve any materials, installations, calibrations checks etc.
19 | Call-out | 9 | Ali Abbas | & Gas
20 | Callout | 9 | Mahdi Ali | QUOTE BAPCO DOCUMENT NUMBER AS WELL
21 | Callout | 9 | Bernard.Grace | Include in reference documents
22 | Callout | 10 | Mahdi Ali | QUOTE BAPCO DOCUMENT NUMBER AS WELL
23 | Call-out | 11 | Ali Abbas | change to RO
24 | Call-out | 11 | Ali Abbas | Nuclear instrumentation
25 | Text Box | 11 | Abdul Majeed | Temperature Gauge
26 | Call-out | 11 | Ali Abbas | Capital O
27 | Call-out | 11 | Bachir M | probe
28 | Text Box | 11 | mohamed.waleed | Where are the FIRE and GAS instruments inspection procedure and QCPs ?
29 | Text Box | 11 | Abdul Majeed | On line flow meters
30 | Text Box | 11 | Abdul Majeed | DP Tx
31 | Call-out | 11 | Ali Abbas | /Analyser Houses?
32 | Text Box | 14 | Abdul Majeed | Seat Leakage test certificate for Tight Shut Off Class 6
33 | Call-out | 15 | Bachir M | #NAME?
34 | Text Box | 15 | Abdul Majeed | and calibration
35 | Text Box | 16 | Abdul Majeed | and calibration
36 | Text Box | 17 | Abdul Majeed | output
37 | Call-out | 19 | Ali Abbas | Note that other FF loops
38 | Text Box | 20 | Abdul Majeed | Seat Leakage Test to be performed for Class 6.
39 | Text Box | 23 | Abdul Majeed | Temperature Gauge
40 | Text Box | 23 | Abdul Majeed | on line flow meter
41 | Text Box | 27 | Abdul Majeed | Cables size is correct
42 | Text Box | 27 | Abdul Majeed | Fan size is correct as per heat cabenit dissipation calculation
43 | Text Box | 31 | Abdul Majeed | and MCM, CCC, BN & WW systems