## 000-J-PQP-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | david.choi | Format of QCF (numbering, head, font, etc.) should be consistent across all QCFs. For example, QCF 1500.P55 and W12 do not follow standard QCF format.
2 | Text Box | 1 | Francis L | Include the verification of ESD and non-ESD Alarm & Trip Test Procedures as part of functional/loop testing. Each procedure will be approved by Owner as as-built documentation upon successful verification as part of functional/loop testing.
3 | Text Box | 1 | 300060 | Line item for Preservation performed after all functioning testing is completed needs adding.
4 | Text Box | 1 | Francis L | Testing of all instrumentation shall be in compliance with project specification BMPS-J31. Include all relevant test/calibration forms including the functional content as per BMPS-J31. As part of the documentation requirement and for carrying out loop checks, each instrument loop shall be provided with an Individual Loop Folder for carrying out loop testing. Any findings and changes shall be recorded on this document. The format and content of Loop Folders shall be in compliance with Clause 8.1 of specification BMPS-J31.
5 | Text Box | 4 | Jong.Ahn | Should include followings; 1. Type of instruments 2. Service description 3. Ref. Drawing number & documents 4. Upstream and down stream piping for straight run requirements. 5. Manufacture 6. Model number 7. Serial number
6 | Callout | 5 | david.choi | Does this mean opening (popping) pressure?
7 | Text Box | 5 | Jong.Ahn | Should include followings: 1. Seat tightness test for steam service, or non-steam service. 2. ASME code stamping
8 | Callout | 5 | david.choi | Unit should be "psig" as per BMPS-A1 Section 13
9 | Callout | 5 | david.choi | Use the correct term (BELLOWS not BELLOW) and clarify the purpose of a design parameter (BELLOWS) in this QCF
10 | Text Box | 6 | Jong.Ahn | Should include followings; 1. Type of instruments 2. Service description 3. Ref. Drawing number & documents 4. check Upstream and down stream piping for straight run requirements. 5. Manufacture 6. Model number 7. Serial number 8. check Flange type and rating 9. check Location of taps 10. check meter material 11. check direction of flow 12. Orifice plate size 13. Bore diameter 14. Plate thickness 15. number of weep holes and their diameter 16. Plate holder material 17. Orifice plates stamp information 18. Installation of transmitter and impulse lines
11 | Text Box | 7 | Jong.Ahn | Should include and specify followings: 1. type of instrument 2. Service description 3. manufacture / model no. / serial no. 4. Installation inspection 5. Primary element installation and calibration 6. Transmitter 7. Impulse line 8. Wiring 9. Wires and terminals tagging at instrument, junction box, marshalling cabinet and input / output cabinet 10. connections and setings are done as shown on the ILD. 11. electrical / air supply 12. Controller 13. Transducer
12 | Text Box | 10 | Jong.Ahn | Need to specify as per the object of this document. Is this for integrated functional test of complex loop or just for field instruments functional test? Couldn't make a sense why C&E required if it is just for field instrument functional test.