## 000-L-TSP-50009-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 7 | David.Jimenez | and isometrics
2 | Call-out | 7 | Raj | Chemical compatibility of the desired service with FRP shall be confirmed prior to fabrication
3 | Call-out | 7 | Raj | Long radius smooth turn elbows shall be used in all cases Standard flanges with neck length adequate to accommodate a butt joint shall be joined to the plain ends of standard elbows
4 | Callout | 7 | JaiMun.Oh | The SUPPLIER shall propose and supply the construction spare and the training pipes.
5 | Text Box | 8 | JaiMun.Oh | SUPPLIER shall provide export permit for Resin and Additives if required. MSDS and the estimated Q'ty for Resin and Additives shall be provided by SUPPLIER for application of import permit.
6 | Callout | 10 | Yousif Ahmadi | or any other tools
7 | Callout | 12 | Yousif Ahmadi | 3.2.1.3
8 | Callout | 16 | David.Jimenez | Is there any criteria (such size, service, etc) to determine whether stress analysis should apply or not? No reference to project general stress specification?
9 | Text Box | 20 | Nalini Mohan | Training to OWNER inspection team shall be provided for field inspection and testing.
10 | Callout | 23 | Yousif Ahmadi | for each 100 length of pipe produced
11 | Callout | 23 | Yousif Ahmadi | for each 100 length of pipe produced
12 | Callout | 23 | Yousif Ahmadi | for each 100 length of pipe produced
13 | Callout | 25 | Yousif Ahmadi | one or Two?
14 | Call-out | 25 | Jawad Alawi | Specify the reference
15 | Callout | 25 | Yousif Ahmadi | Which paragraph?? There is no 9.2.1
16 | Callout | 27 | Yousif Ahmadi | Per AWWA below to be included: (1) the phrase ANSI/AWWA C950; (2) nominal pipe size, cell classification, and diameter series; (3) AWWA pressure class; (4) stiffness class; and (5) manufacturer’s mark and identity code Check and confirm
17 | Callout | 27 | JaiMun.Oh | Spool Piece Number
18 | Text Box | 30 | Nalini Mohan | Since this class of piping is used for oily water sewer maximum temperature faced due to draining of hot liquids (during plant upset condition) shall be ascertained and informed to supplier. Currently RXB30 limits the design temperature to 165degF. During upset conditions liquids beyond 165degF will be drained to sewer system.