## 000-M-STD-50004-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Antony.Bentley | TYP. throughout 'STIFFENER'
2 | Text Box | 1 | Antony.Bentley | abbreviation for?
3 | Callout | 1 | Chandrahasan D | USE ABBREVIATIONS ALREADY DEFINED IN STANDARD DWG. OTHERSIWDE USE FULL TEXT.
4 | Callout | 1 | Salman Almajed | Is the force designation required on standard drawing? If it is required then please show it on all connection types.
5 | Callout | 1 | Erwin.Lugue | Show in hidden lines
6 | Callout | 1 | Erwin.Lugue | Show in hidden lines
7 | Cloud+ | 1 | Salman Almajed | Change the break line to reflect tube section.
8 | Text Box | 1 | Salman Almajed | General comments: - The drawing has many text and dimensions placed on top of drawing lines making it difficult to read. - Add reference drawing "General notes for steel structures".
9 | Callout | 1 | Erwin.Lugue | Specify thickness of the fin plates
10 | Callout | 1 | Erwin.Lugue | No stiffeners on the other side?
11 | Callout | 1 | Erwin.Lugue | Stiffen the web of the column
12 | Cloud+ | 1 | MAK | Delete
13 | Text Box | 1 | Antony.Bentley | TYP. throughout 'GAUGE'
14 | Cloud+ | 1 | MAK | NTS
15 | Callout | 1 | Erwin.Lugue | Provide dimensions of bolts end distances & spacings
16 | Text Box | 1 | Erwin.Lugue | The connections does not permit partial end rotations. Connections will then be designed to the 90% element capacity?
17 | Text Box | 1 | Erwin.Lugue | Provide section views to see bolt arrangements
18 | Callout | 1 | Erwin.Lugue | Provide stiffener plates
19 | Cloud+ | 1 | Salman Almajed | Why is this angle zero?
20 | Text Box | 1 | Salman Almajed | 10
21 | Text Box | 1 | MAK | General Comment: All the texts in drawings shall be searchable and in UPPERCASE. Text fonts and styles shall be as per BMPS-A8.
22 | Callout | 1 | Salman Almajed | All hidden elements should be represented by dashed lines (Typical comment).
23 | Callout | 1 | Chandrahasan D | What about stiffeners if any required? Will it be covered in separate details
24 | Callout | 1 | Erwin.Lugue | stiffener plates
25 | Callout | 1 | Erwin.Lugue | Stiffen the web of columns
26 | Text Box | 1 | Erwin.Lugue | For the vertical bracing details it is necessary to splice the flanges not only the webs to develop the required capacity
27 | Cloud+ | 1 | Salman Almajed | Duplicate text
28 | Callout | 1 | Chandrahasan D | What about stiffeners if any required? Will it be covered in separate details (Typ)
29 | Callout | 1 | Joon Cho | WP (Working Point) typical
30 | Callout | 1 | Chandrahasan D | Stiffeners missing in this detail??