## 000-M-TSP-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Erwin.Lugue | General comment: Client preference are the Eurocodes. Document was reviewed according to the American codes. However, provide a statement that the use of the American codes had been approved by BAPCO
2 | Cloud+ | 1 | MAK | BOD shall be used for BASIS OF DESIGN
3 | Text Box | 1 | Salman Almajed | <General comment> There are many formatting errors in this document. Contractor to proofread the whole document and correct these errors.
4 | Text Box | 1 | Antony.Bentley | SHALLOW
5 | Cloud+ | 2 | Erwin.Lugue | Optional code (not to mix with the American codes)
6 | Callout | 2 | Chandrahasan D | <add>Process Industry Practices (PIPs)
7 | Callout | 6 | Mahdi Ali | USE BAPCO NUMBERS
8 | Call-out | 8 | Hasan Al Noaimi | RSCB
9 | Call-out | 8 | Hasan Al Noaimi | South
10 | Callout | 8 | Joon Cho | Not clear, Applicable Codes and Standard and Applicable all material specifications shall be stipulated clearly and all those shall be approved by Owner.
11 | Callout | 8 | Bader Abdulrahman | Explain the basis of choosing ACI codes rather than BS-EN).
12 | Cloud+ | 9 | Erwin.Lugue | Not in line with the LRFD
13 | Text Box | 11 | Erwin.Lugue | Remove irrelevant tests
14 | Callout | 12 | Chandrahasan D | LIst applicable Process Industry practices
15 | Cloud+ | 12 | Erwin.Lugue | In line with ANSI/ASTM?
16 | Cloud+ | 13 | Erwin.Lugue | Optional code
17 | Cloud+ | 13 | Erwin.Lugue | These are standard details for tanks
18 | Callout | 14 | Joon Cho | <Add> Plant Datum & Coordination System (Dwg. No. 000-A-PPN-60006-001 Rev. 0 IFC)
19 | Cloud+ | 14 | Erwin.Lugue | These are standard details for tanks
20 | Cloud+ | 14 | Salman Almajed | "Bahrain" - this typo is repeated across many transmittals
21 | Text Box | 15 | Erwin.Lugue | All in-house developed spreadsheets shall be verified and approved by client
22 | Text Box | 15 | Erwin.Lugue | Develop a common format and specific tools to be used in all design calculation documents (FEA Modelling, Steel Structures, & Foundations,etc.) to be implemented in all OC's
23 | Callout | 15 | Erwin.Lugue | permanent
24 | Cloud+ | 15 | Erwin.Lugue | What is this document?
25 | Cloud+ | 16 | Erwin.Lugue | Include in the basic load cases
26 | Cloud+ | 16 | Erwin.Lugue | Section 13
27 | Text Box | 16 | Erwin.Lugue | Sub-grade modulus? Permissible soil bearing pressure & settlement (total)?
28 | Text Box | 16 | Erwin.Lugue | List all the design parameters per area (if required)
29 | Cloud+ | 16 | Erwin.Lugue | Values depending on the soil type
30 | Callout | 16 | Bernard.Grace | Clear headroom
31 | Text Box | 17 | Erwin.Lugue | Include all basic load cases in the load combinations
32 | Cloud+ | 17 | Erwin.Lugue | /Dynamic Loads?
33 | Callout | 17 | Erwin.Lugue | Structure selfweight
34 | Cloud+ | 17 | Erwin.Lugue | Clarify this load
35 | Text Box | 17 | Erwin.Lugue | Arrange sequentially all the basic load cases in accordance with the next section (description of loads)
36 | Text Box | 17 | Erwin.Lugue | Unreinforced concrete
37 | Callout | 17 | Erwin.Lugue | 24? Verify
38 | Text Box | 17 | Erwin.Lugue | Impact load missing? Blast load missing?
39 | Cloud+ | 18 | Erwin.Lugue | Verify weight depending on the thickness of checkered plate & type of grating
40 | Callout | 19 | Salman Almajed | Add comma "," or semicolon ";"
41 | Callout | 19 | Salman Almajed | Why this sentence is shown in new line?
42 | Callout | 19 | Salman Almajed | ground-supported
43 | Cloud+ | 19 | Erwin.Lugue | only S.I. units
44 | Text Box | 20 | Bader Abdulrahman | Should be mentioned in BOLD. Also "e" must be subscript
45 | Cloud+ | 20 | Salman Almajed | Why many sentences are incomplete? Please proofread the document.
46 | Callout | 22 | Erwin.Lugue | service load
47 | Callout | 23 | Erwin.Lugue | or contraction
48 | Callout | 24 | Salman Almajed | As per Chevron guideline CIV-EN-300 (sec. 321 ch. 10), the coefficient of friction shall have the value of 0.42 for 1 or 2 pipes and 0.3 for 3 or more pipes. Contractor to clarify as per codes and standards the background behind the use of 0.3 coefficient for 1 pipe and 0.1 for multiple pipes.
49 | Cloud+ | 24 | Salman Almajed | 42.2
50 | Cloud+ | 24 | Erwin.Lugue | And as per BMPS standard mechanical details
51 | Cloud+ | 24 | Salman Almajed | 6.2
52 | Cloud+ | 24 | Salman Almajed | 8.9
53 | Cloud+ | 24 | Salman Almajed | Please revise the calculation using 42.2 deg. C. (highest) and 8.9 deg. C. (lowest), as per sec. 6.6 of BMPS-A1
54 | Text Box | 25 | Erwin.Lugue | Include consideration of bundle pull for stacked equipments
55 | Cloud+ | 26 | Erwin.Lugue | structure & foundations
56 | Cloud+ | 26 | Salman Almajed | Why is it in new line?
57 | Cloud+ | 27 | Erwin.Lugue | All load combinations shall be developed and agreed with the client
58 | Text Box | 27 | Erwin.Lugue | Include the buoyant force
59 | Text Box | 27 | Erwin.Lugue | Develop Load combinations (Service & Strength Combinations) for: - Buildings load combinations w/ blast loads - Shelters w/ Crane Loads - Foundations for Reciprocating & Rotary Equipment w/ dynamic loads
60 | Callout | 27 | Chandrahasan D | <add> Loads due to settlement soil strata
61 | Cloud+ | 27 | Erwin.Lugue | Based from the QRA report
62 | Callout | 28 | Salman Almajed | Add (Test Weight + Live Load) L.C.
63 | Cloud+ | 28 | Salman Almajed | According to ASCE/SEI 7-10, basic combination is 0.6D+0.6W (sec. 2.4.1 combination no. 7). Hence, LC-3 should be 0.6(DS+De)+0.6W & LC-4 should be 0.6(Ds+Df)+0.6Wp
64 | Cloud+ | 29 | Salman Almajed | According to ASCE/SEI 7-10, basic combination is 0.6D+0.6W (sec. 2.4.1 combination no. 7). Hence, LC-4 should be 0.6(DS+De)+0.6W & LC-5 should be 0.6(Ds+Df)+0.6Wp
65 | Callout | 29 | Salman Almajed | Add (Test Weight + Live Load) L.C.
66 | Text Box | 30 | Salman Almajed | (b)
67 | Cloud+ | 30 | Salman Almajed | Contractor to clarify the reduction factor of "0.6" for wind load, as per the relevant codes and standards.
68 | Callout | 31 | Salman Almajed | less
69 | Callout | 31 | Salman Almajed | 10025
70 | Cloud+ | 31 | Erwin.Lugue | Design philosophy not to be mixed
71 | Cloud+ | 31 | Salman Almajed | 10025
72 | Cloud+ | 31 | Salman Almajed | Why this sentence is not complete?
73 | Callout | 31 | Chandrahasan D | Verify painting vs Galvanizing for Handrails
74 | Text Box | 31 | Erwin.Lugue | Provide specifically all characteristic mechanical properties for use in design calculations- a common design parameters for all OC's
75 | Cloud+ | 32 | Salman Almajed | Why this sentence is not complete?
76 | Callout | 32 | Salman Almajed | Decking should have the strength required to resist lateral torsional buckling of floor beams. Include the code requirement in this paragraph.
77 | Text Box | 33 | Erwin.Lugue | Provide specifically all characteristic mechanical properties of bolts for use in design calculations- a common design parameters for all OC's
78 | Callout | 33 | Chandrahasan D | <Revise> High Strength bolts
79 | Cloud+ | 33 | Salman Almajed | Why this word is in new line?
80 | Cloud+ | 34 | Erwin.Lugue | Mixed ASD & LRFD?
81 | Text Box | 34 | Bader Abdulrahman | L being the span of the beam
82 | Text Box | 35 | Erwin.Lugue | Include specifications for painting & corrosion protection
83 | Callout | 35 | Chandrahasan D | serrated for all walkways and plain for others
84 | Text Box | 36 | Erwin.Lugue | Include an option for possibility of modular construction
85 | Cloud+ | 36 | Erwin.Lugue | optional
86 | Cloud+ | 36 | Erwin.Lugue | optional
87 | Cloud+ | 37 | Erwin.Lugue | prior
88 | Cloud+ | 38 | Salman Almajed | use S.I. units only
89 | Cloud+ | 39 | Salman Almajed | 0.6-0.9
90 | Text Box | 39 | Erwin.Lugue | Add refractory concrete or heat resistant concrete requirements (as required in the areas of fired heaters)
91 | Cloud+ | 39 | Erwin.Lugue | Sulfate resisting portland cement
92 | Cloud+ | 39 | Salman Almajed | What is (**)?
93 | Text Box | 40 | Bader Abdulrahman | to
94 | Callout | 40 | Erwin.Lugue | Too general, Provide specifically all characteristic mechanical properties for use in design calculations- a common format for all OC's to have the same values in all the reports
95 | Cloud+ | 40 | Salman Almajed | According to BMPS-M2 Sec. 16.11.1: Cover to all other external exposed concrete faces = 65 mm. Cover to all other internal protected faces = 50 mm. Cover of exposed suspended upper slab of building = 40 mm
96 | Callout | 40 | Joon Cho | <Add> and other concrete facilities at the cooling towers, the whole Sulphur handling facility (SHF), OWS/CSS/CS Basins, all concrete structures at C3/C4 Bullets, all concrete structures exposed to marine environment,
97 | Cloud+ | 40 | Erwin.Lugue | optional
98 | Callout | 43 | Joon Cho | <Recommendation> In case of sensitive settlement requirements for specific equipment or mechanical facilities (e.g Large storage tanks (over 30 m-dia.), mounded storage bullet, specific storage pits, etc.) other than aforementioned settlement, EPC Contractor shall specify separately.
99 | Cloud+ | 43 | Erwin.Lugue | only S.I. units
100 | Text Box | 44 | Erwin.Lugue | Note: Most software programs such as Staadfoundation uses the conventional /rigid method of analysis.
101 | Cloud+ | 46 | Erwin.Lugue | F1554 ASTM36 hot dipped galvanized?
102 | Cloud+ | 46 | Salman Almajed | Incomplete sentence
103 | Cloud+ | 46 | Erwin.Lugue | in kN/m3
104 | Cloud+ | 48 | Erwin.Lugue | Provide refractory concrete specification
105 | Text Box | 49 | Erwin.Lugue | Specify total permissible settlement
106 | Cloud+ | 53 | Salman Almajed | 0.7 to 1.3 (refer tender clarification - T87)
107 | Text Box | 54 | Erwin.Lugue | Verify if corrosion allowance is required especially near the coastal areas
108 | Cloud+ | 54 | Salman Almajed | Please correct the grammar mistake.
109 | Text Box | 55 | Salman Almajed | Design of deep foundations (piles) is not shown in this document. We are advised it will be in a separate documentation. Please advise.
110 | Cloud+ | 56 | Erwin.Lugue | Permissible design ratio to be decided by the owner
111 | Cloud+ | 56 | Salman Almajed | Add PIP STC01015 in CODES AND STANDARDS section of this document.
112 | Cloud+ | 58 | Salman Almajed | Program
113 | Text Box | 59 | Erwin.Lugue | Missing load combinations for: Other non-building structures (Process structures, equipment platforms, etc.) Buildings with blast loads Machine foundations w/ dynamic loads
114 | Cloud+ | 60 | Erwin.Lugue | ASCE 7-10 Considers bi-directional wind action
115 | Cloud+ | 62 | Salman Almajed | According to ASCE/SEI 7-10, basic combination is 0.6D+0.6W (sec. 2.4.1 combination no. 7). Hence, LC 1004-1007 should have factor of 0.6 for Ds & Do
116 | Cloud+ | 62 | Erwin.Lugue | ASCE 7-10 considers bi-directional wind action
117 | Text Box | 66 | Erwin.Lugue | Wind considerations not covered in this basis of design shall refer to Wind load ASCE recommendations for petrochemical facilities
118 | Text Box | 69 | Erwin.Lugue | To include additional wind load considerations as per sec 4.2.6 of the ASCE Wind loads for Petrochemical & Other Facilities
119 | Text Box | 72 | Erwin.Lugue | To include Richart's chart for limits of vertical vibration or amplitude