## 000-P-PHD-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Ebrahim | , SPECIFICATION BMPS-P1, CLAUSE 7.
2 | Call-out | 1 | Ebrahim | 1. Remove this point as it will be covered at point 2 above. 2. ADD the following: MAIN POWER EARTHING ELECTRODES SHALL BE PROVIDED AT THE SUBSTATION, AND (EMERGENCY GENERATOR IF APPLICABLE). THE MAXIMUM VALUES OF INDIVIDUAL ELECTRODE SYSTEMS TO THE BODY OF EARTH SHALL BE 1.0 OHM.
3 | Call-out | 1 | CK Samy | All air termination rods shall be interconnected. Cleats and clamps shall be provided at suitable interval for horizontal & vertical conductors.
4 | Text Box | 1 | Mohamed Aldoseri | cellar
5 | Text Box | 1 | Jongman.Kim | Contractor Reference Drawing Block shall be provided as per BMPS-A8, section 6.3.7.
6 | Text Box | 1 | Jongman.Kim | Contractor shall make sure that drawing No. complies with the requirement of BMPS-A8, section 6.3.4, Text Style of Drawing No. shall be T3.
7 | Text Box | 1 | Mohamed Aldoseri | Delete HV
8 | Text Box | 1 | Mohamed Aldoseri | earth bar connection is required-Typical
9 | Call-out | 1 | Mohamed Aldoseri | Earth bar to be used-Typical
10 | Call-out | 1 | Mohamed Aldoseri | FEED
11 | Text Box | 1 | Jongman.Kim | Following shall be added: - Telecommunication Grounding - Intrinsic safety Grounding
12 | Call-out | 1 | CK Samy | Include following generator notes 1.Earthing conductor crossing the road shall be laid in hume pipe or at a greater depth to avoid damage. 2. When earthing conductor passes through floor walls etc., suitable sleeves shall be provided and same shall be sealed after installation. 3. earthing conductor shall be laid at a distance of 1.5m from the building /boundary wall . 4. Earthing conductor shall be covered by cover of good soil free from rocks and debris. 5. Flexible earth conductor shall be provided at expansion joints for earthing gates ,operating handles etc., 6. Typical grounding of bus duct shall be indicated. 7. Connection between lightning down conductor and ground rod shall be made via test link located 2000mm above ground. 8. Over head shelter crane grounding shall be indicated.
13 | Call-out | 1 | Mohamed Aldoseri | Include the pipe in the Legend table with its description
14 | Text Box | 1 | Jongman.Kim | Lightning protection shall be provided for the rack room building.
15 | Text Box | 1 | Mohamed Aldoseri | philosophy should use earth bar. Refer to BMPS-P-50603, p28-Typical
16 | Text Box | 1 | Jongman.Kim | PROTECTION
17 | Call-out | 1 | Mohamed Aldoseri | Show a typical number of earth connections for 1 item on this drawing (ex:Pipe rack)
18 | Call-out | 1 | CK Samy | Spacing between instrument grounding rod shall be indicated in the notes.
19 | Call-out | 1 | Mohamed Aldoseri | Street lighting Pole
20 | Call-out | 1 | CK Samy | Suitable size shall be selected to withstand transformer fault current (Typical)
21 | Text Box | 1 | Mohamed Aldoseri | The fence around the cable cellar shall be grounded.
22 | Call-out | 1 | Mohamed Aldoseri | The Philosophy of grounding/earthing system shall be using earth bar where applicable. Refer to BMPS-P-50603 and show the same philosophy in this drawings.
23 | Text Box | 1 | Mohamed Aldoseri | The spacing between grounding electrode shall be at least 2400 MM.
24 | Call-out | 1 | Mohamed Aldoseri | This line to be defined or deleted.
25 | Text Box | 1 | Jongman.Kim | To be filled-up
26 | Text Box | 1 | Mohamed Aldoseri | UPS grounding,refer to BMPS- P16.
27 | Pen | 1 | Jongman.Kim | w
28 | Text Box | 1 | Jongman.Kim | With regard to the main grounding grid cable size, - as per BMPS-P-50603 (Grounding System Typical Installation Standard), the main earthing loop shall be 120 sqmm - as per Note 4 of FEED Document No. BRA-231688 (Overall Main Grounding Layout, Refinery South), the main grounding grid shall be carried out by means of PVC insulated flexible copper conductor 120 sqmm. In this regard, Contractor shall clarify and revise the drawing, accordingly.